## Worksheet
SRB206SQ 24V AC/DC
2 safety contacts, STOP 0 6 Signalling outputs Multi-evaluation of up to 6 safety guards Suitable for the signal processing of outputs with contact sensors
Ordering data
Note (Delivery capacity) | Not available!
Product type description | SRB206SQ 24V AC/DC
Article number (order number) | 101173934
EAN (European Article Number) | 4250116201877
eCl@ss number, version 12.0 | 27-37-18-19
eCl@ss number, version 11.0 | 27-37-18-19
eCl@ss number, version 9.0 | 27-37-18-19
ETIM number, version 7.0 | EC001449
ETIM number, version 6.0 | EC001449
Approvals - Standards
Certificates | cULus
General data
Standards | EN IEC 62061 EN ISO 13849-1 EN IEC 60947-5-1 EN IEC 60947-5-3 EN IEC 60947-5-5 EN IEC 61508 EN IEC 60204-1 EN IEC 60947-1
Climatic stress | EN 60068-2-78
Housing material | Glass-fibre reinforced thermoplastic, ventilated
Gross weight | 400 g
General data - Features
Electronic Fuse | Yes
Wire breakage detection | Yes
Cross-circuit detection | Yes
Removable Terminals | Yes
Start input | Yes
Feedback circuit | Yes
Automatic reset function | Yes
Reset edge detection | Yes
Reset after disconnection of supply voltage | Yes
Earth connection detection | Yes
Integral system diagnostics, status | Yes
Number of auxiliary contacts | 6
Number of LEDs | 4
Number of normally closed (NC) | 12
Number of safety contacts | 2
Number of signalling outputs | 6
<table><tr><td>Safety classification</td></tr></table>
Standards | EN IEC 60947-5-1 EN IEC 61508
Stop-Category | 0
<table><tr><td>Safety classification - Relay outputs</td></tr></table>
Performance Level, stop 0, up to | d
Category, Stop 0 | 3
Diagnostic Coverage (DC) Level, Stop 0 | > 60 %
PFH value, Stop 0 | 2.00 x 10⁻⁷ /h
Safety Integrity Level (SIL), Stop 0, suitable for applications in | 2
Mission time | 20 Year(s)
Common Cause Failure (CCF), minimum | 65
Mechanical data
Mechanical lifetime, minimum | 10,000,000 Operations
Mounting | Snaps onto standard DIN rail to EN 60715
Mechanical data - Connection technique
Terminal designations | IEC/EN 60947-1
Cable section, minimum | 0.25 mm²
Cable section, maximum | 2.5 mm²
Tightening torque of Clips | 0.6 Nm
Allowed type of cable | solid single-wire flexible
Terminal (mechanical) | Schraubklemmen
Mechanical data - Dimensions
Width | 45 mm
Height | 100 mm
Depth | 121 mm
Ambient conditions
Degree of protection of the enclosure | IP40
Degree of protection of the installation space | IP54
Degree of protection of clips or terminals | IP20
Ambient temperature | -25 ... +45 °C
Storage and transport temperature | -40 ... +85 °C
Resistance to vibrations | 10...55 Hz, Amplitude 0.35 mm, ± 15 %
Restistance to shock | 30 g / 11 ms
Ambient conditions - Insulation values
Rated impulse withstand voltage Uimp | 4 kV
Overvoltage category | III
Degree of pollution | 2
Electrical data
Frequency range | 50 Hz 60 Hz
Operating voltage | 24 VAC -15 % / +10 %24 VDC -15 % / +20 %
Ripple voltage | 10 %
Rated operating voltage | 24 VAC
Rated operating voltage | 24 VDC
Operating current | 275 mA
Rated AC voltage for controls, 50 Hz, minimum | 20.4 VAC
Rated control voltage at AC 50 Hz, maximum | 26.4 VAC
Rated AC voltage for controls, 60 Hz, minimum | 20.4 VAC
Rated control voltage at AC 60 Hz, maximum | 26.4 VAC
Rated AC voltage for controls at DC minimum | 20.4 VDC
Rated control voltage at DC, maximum | 28.8 VDC
Utilisation category AC-15 | 230 VAC
Utilisation category AC-15 | 6 A
Utilisation category DC-13 | 24 VDC
Utilisation category DC-13 | 6 A
Electrical power consumption | 3.6 W
Electrical power consumption | 6.6 VA
Contact resistance, maximum | 0.1 Ω
Note (Contact resistance) | in new state
Drop-out delay in case of &quot;emergency stop&quot;, maximum | 30 ms
Pull-in delay at RESET, typically | 50 ms
Material of the contacts, electrical | AgCdO, self-cleaning, positive drive
Electrical data - Digital inputs
Conduction resistance, maximum | 40 Ω
Electrical data - Electromagnetic compatibility (EMC)
EMC rating | EMC-Directive
Status indication
Indicated operating states | Position relay K2 Position relay K1 Internal operating voltage Ui
Other data
Note (applications) | Guard system Emergency-Stop button Pull-wire emergency stop switches
Note
Note (General) | Inductive loads (e.g. contactors, relays, etc.) are to be suppressed by means of a suitable circuit.
Wiring example
Note (Wiring diagram) | The wiring diagram is shown with guard doors closed and in de-energised condition. Automatic start: The automatic start is programmed by connecting the feedback circuit to the terminals X1/X3. If the feedback circuit is not required, establish a bridge. Relay outputs: Suitable for 2 channel control, for increase in capacity or number of contacts by means of contactors or relays with positive-guided contacts. The control recognises cross-short, cable break and earth leakages in the monitoring circuit. Input level: The example shows a 2-channel control of a guard door monitoring with two position switches, whereof one with positive break, external reset button (R); cross-wire monitoring and feedback circuit (H2) If more guard doors are monitored, they must be connected according to the wiring table A single failure in the sensors does not cause the safety to be lost If the single failure occurs, the safety function will be maintained. Some, although not all, errors will be recognised. An accumulation of unrecognised errors could cause the safety function to be lost.
Schmersal Canada Ltd., 29 Centennial Road, Unit 1, Orangeville, Ontario L9W 1R1 Canada
The details and data referred to have been carefully checked. Images may diverge from original. Further technical data can be found in the manual. Technical amendments and errors possible.
Generated on: 2025-10-13, 10:15 a.m.