## Worksheet
CSS 12-34-V-D-M-ST
| 1 x connector plug M12, 8-pole Actuation from top Max. 31 sensors can be wired in series. Thermoplastic enclosure Electronic contact-free, coded system Misaligned actuation possible | 27 mm x 108.2 mm x 35 mm High repeat accuracy of the switching points Max. length of the sensor chain 200 m 2 short-circuit proof PNP safety outputs Integral cross-short, wire-breakage and external voltage monitoring of the safety cables up to the control cabinet
Ordering data
Product type description | CSS 12-34-V-D-M-ST
Article number (order number) | 101181065
EAN (European Article Number) | 4030661314884
eCl@ss number, version 12.0 | 27-27-46-01
eCl@ss number, version 11.0 | 27-27-24-03
eCl@ss number, version 9.0 | 27-27-24-03
ETIM number, version 7.0 | EC001829
ETIM number, version 6.0 | EC001829
Approvals - Standards
Certificates | TÜV cULus UKCA
General data
Standards | EN IEC 60947-5-3
Working principle | inductive
Housing construction form | Block
Installation conditions (mechanical) | not flush
Sensor topology | Sensor for series wiring
Housing material | Glass-fibre, reinforced thermoplastic
Active area | Glass-fibre, reinforced thermoplastic
Reaction time, maximum | 30 ms
Duration of risk, maximum | 60 ms
Gross weight | 140 g
General data - Features
Diagnostic output | Yes
Short circuit detection | Yes
Cross-circuit detection | Yes
Safety functions | Yes
Cascadable | Yes
Integral system diagnostics, status | Yes
Number of LEDs | 3
Number of semi-conductor outputs with signaling function | 1
Number of fail-safe digital outputs | 2
Number of series-wiring of sensors | 31
<table><tr><td>Safety classification</td></tr></table>
Standards | EN ISO 13849-1 EN IEC 60947-5-3 EN IEC 61508
Performance Level, up to | e
Category | 4
PFH value | 3.60 x 10⁻⁹ /h
Safety Integrity Level (SIL), suitable for applications in | 3
Mission time | 20 Year(s)
Mechanical data
Actuating panels | Actuation from top
Active area | front side
Switching distance actuator | Actuator CST 34-V-1: 12 mm (typical switch distance Sn) Actuator CST 34-V-1: 10 mm (ensured switch distance ON Sao) Actuator CST 34-V-1: 15 mm (ensured switch distance OFF Sar) Actuator CST 34-S-1 / CST 34-S-3: 15 mm (typical switch distance Sn) Actuator CST 34-S-1 / CST 34-S-3: 13 mm (ensured switch distance ON Sao) Actuator CST 34-S-1 / CST 34-S-3:: 18 mm (ensured switch distance OFF Sar) Actuator CST 34-S-2: 10 mm (typical switch distance Sn) Actuator CST 34-S-2: 8 mm (ensured switch distance ON Sao) Actuator CST 34-S-2: 16 mm (ensured switch distance OFF Sar) Actuator CST 180-1 / CST 180-2: 12 mm (typical switch distance Sn) Actuator CST 180-1 / CST 180-2: 10 mm (ensured switch distance ON Sao) Actuator CST 180-1 / CST 180-2: 16 mm (ensured switch distance OFF Sar)
Mechanical data - Switching distances according EN IEC 60947-5-3
Hysteresis (Switching distance), maximum | 1.5 mm
Repeat accuracy R | 0.5 mm
Note (Repeat accuracy R) | Axial offset: the front face allows for an axial misalignment (z) of max. ± 8 mm (see figure: operating principle).
Mechanical data - Connection technique
Note (length of the sensor chain) | Cable length and cross-section change the voltage drop dependiing on the output current
Note (series-wiring) | Unlimited number of devices, oberserve external line fusing, max. 31 devices in case of serial diagnostic SD
Termination | Connector plug M12, 8-pole
Wire cross-section | 22 AWG
Mechanical data - Dimensions
Length of sensor | 35 mm
Width of sensor | 27 mm
Height of sensor | 108.2 mm
Ambient conditions
Degree of protection | IP65 IP67
Ambient temperature | -25 ... +70 °C
Storage and transport temperature | -25 ... +85 °C
Resistance to vibrations | 10 … 55 Hz, amplitude 1 mm
Restistance to shock | 30 g / 11 ms
Protection class | II
Ambient conditions - Insulation values
Rated insulation voltage Ui | 32 VDC
Rated impulse withstand voltage Uimp | 0.8 kV
Overvoltage category | III
Degree of pollution | 3
Electrical data
No-load supply current I0, typical | 100 mA
Operating current | 600 mA
Required rated short-circuit current | 100 A
Utilisation category DC-12 | 24 VDC
Utilisation category DC-12 | 0.05 A
Utilisation category DC-13 | 24 VDC
Utilisation category DC-13 | 0.05 A
Note (Electrical data, Fuse rating) | (Circuit breaker)
Switching frequency, approx. | 3 Hz
Utilisation category DC-12 | 24 VDC / 0.05 A
Electrical data - Safety digital outputs
Rated operating current (safety outputs) | 250 mA
Output current, (fail-safe output), maximum | 0.25 A
Design of control elements | p-type
Voltage drop Ud, maximum | 0.5 V
Leakage current Ir, maximum | 0.5 mA
Voltage, Utilisation category DC-12 | 24 VDC
Current, Utilisation category DC-12 | 0.25 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 0.25 A
Electrical data - Diagnostic outputs
Design of control elements | p-type
Voltage drop Ud, maximum | 5 V
Voltage, Utilisation category DC-12 | 24 VDC
Current, Utilisation category DC-12 | 0.05 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 0.05 A
Electrical data - Electromagnetic compatibility (EMC)
Interfering radiation | IEC 61000-6-4
EMC rating | IEC 61000-6-2
Pin assignment
PIN 1 | 1A1 Ue: (1)
PIN 2 | X1 Safety input 1
PIN 3 | A2 GND
PIN 4 | Y1 Safety output 1
PIN 5 | OUT Diagnostic output OUT
PIN 6 | X2 Safety input 2
PIN 7 | Y2 Safety output 2
PIN 8 | IN without function
Scope of delivery
Scope of delivery | Actuator must be ordered separately.
Accessory
Recommendation (actuator) | CST 34-V-1 CST 34-S-2 CST 34-S-3 CST 180-1 CST 180-2
Recommended safety switchgear | PROTECT PSC1 SRB-E-301ST SRB-E-201LC
Note
Note (General) | Evaluation requirements: dual-channel safety input, suitable for p-type sensors with NO function. The safety-monitoring module must tolerate internal functional tests of the sensors with cyclic switch-off of the sensor outputs for max. 0.5 ms. Short-circuit recognition by the evaluation is not necessary.
Schmersal Canada Ltd., 29 Centennial Road, Unit 1, Orangeville, Ontario L9W 1R1 Canada
The details and data referred to have been carefully checked. Images may diverge from original. Further technical data can be found in the manual. Technical amendments and errors possible.
Generated on: 2024-05-24, 6:51 p.m.