## Worksheet
CSS 8-180-2P+D-E-L
| Pre-wired cable 5-pole Comfortable diagnostics through sensor LED and electronic signalling output Thermoplastic enclosure Electronic contact-free, coded system Misaligned actuation possible | High repeat accuracy of the switching points Max. length of the sensor chain 200 m Early warning when operating near the limit of the sensor's hysteris range Self-monitoring series-wiring of 16 sensors 2 short-circuit proof PNP safety outputs
Ordering data
Product type description | CSS 8-180-2P+D-E-L
Article number (order number) | 101169552
EAN (European Article Number) | 4030661295954
eCl@ss number, version 12.0 | 27-27-46-01
eCl@ss number, version 11.0 | 27-27-24-03
eCl@ss number, version 9.0 | 27-27-24-03
ETIM number, version 7.0 | EC001829
ETIM number, version 6.0 | EC001829
Approvals - Standards
Certificates | TÜV cULus UKCA
General data
Standards | EN IEC 60947-5-3 EN IEC 61508
Working principle | inductive
Housing construction form | Cylinder, thread
Installation conditions (mechanical) | not flush
Sensor topology | Individual sensor or end sensor in a series
Housing material | Glass-fibre, reinforced thermoplastic
Active area | Glass-fibre, reinforced thermoplastic
Material of the nuts | Glass-fibre, reinforced thermoplastic
Reaction time, maximum | 30 ms
Duration of risk, maximum | 30 ms
Gross weight | 150 g
General data - Features
Short circuit detection | Yes
Cross-circuit detection | Yes
Safety functions | Yes
Integral system diagnostics, status | Yes
Number of semi-conductor outputs with signaling function | 1
Number of fail-safe digital outputs | 2
Number of series-wiring of sensors | 16
<table><tr><td>Safety classification</td></tr></table>
Standards | EN ISO 13849-1 EN IEC 60947-5-3 EN IEC 61508
Performance Level, up to | e
Category | 4
PFH value | 2.50 x 10⁻⁹ /h
Safety Integrity Level (SIL), suitable for applications in | 3
Mission time | 20 Year(s)
Mechanical data
Tightening torque of nuts, maximum | 3 Nm
Mechanical data - Switching distances according EN IEC 60947-5-3
Switch distance, typical | 8 mm
Assured switching distance &quot;ON&quot; Sao | 7 mm
Assured switching distance &quot;OFF&quot; Sar | 10 mm
Hysteresis (Switching distance), maximum | 0.7 mm
Repeat accuracy R | 0.2 mm
Mechanical data - Connection technique
Length of cable | 2 m
Termination | Cable
Terminal connector, Output | 5-pole
Wire cross-section | 0.35 mm2
Wire cross-section | 22 AWG
Mechanical data - Dimensions
ISO thread of the sensor | M18
width across flats | 24 BK
Length of sensor | 92 mm
Ambient conditions
Degree of protection | IP65 IP67
Ambient temperature | -25 ... +60 °C
Storage and transport temperature | -25 ... +85 °C
Resistance to vibrations | 10 … 55 Hz, amplitude 1 mm
Restistance to shock | 30 g / 11 ms
Protection class | II
Ambient conditions - Insulation values
Rated insulation voltage Ui | 32 VDC
Rated impulse withstand voltage Uimp | 0.8 kV
Overvoltage category | III
Degree of pollution | 3
Electrical data
Operating voltage | 24 VDC -15 % / +10 %
No-load supply current I0, typical | 50 mA
Rated operating voltage | 24 VDC
Operating current | 1,000 mA
Switching frequency, approx. | 3 Hz
Utilisation category DC-12 | 24 VDC / 0.05 A
Electrical data - Safety digital outputs
Rated operating current (safety outputs) | 500 mA
Output current, (fail-safe output), maximum | 0.5 A
Design of control elements | p-type
Voltage drop Ud, maximum | 0.5 V
Leakage current Ir, maximum | 0.5 mA
Voltage, Utilisation category DC-12 | 24 VDC
Current, Utilisation category DC-12 | 0.5 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 0.5 A
Electrical data - Diagnostic outputs
Rated operating voltage | 24 VDC
Design of control elements | p-type
Voltage drop Ud, maximum | 4 V
Voltage, Utilisation category DC-12 | 24 VDC
Current, Utilisation category DC-12 | 0.05 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 0.05 A
Status indication
Note (LED switching conditions display) | Multi-coloured LED: Green, Red, Yellow
Pin assignment
PIN 1 | A1 Ue Brown
PIN 2 | Y2 safety output 2: White
PIN 3 | A2 GND Blue
PIN 4 | Y1 Safety output 1 Black
PIN 5 | signalling output: Grey
Scope of delivery
Scope of delivery | Actuator must be ordered separately.
Scope of delivery of mounting material | 2x nuts M18 x 1
Accessory
Recommendation (actuator) | CST 180-1 CST 180-2
Recommended safety switchgear | PROTECT PSC1 SRB-E-301ST SRB-E-201LC
Note
Note (General) | Evaluation requirements: dual-channel safety input, suitable for p-type sensors with NO function. The safety-monitoring module must tolerate internal functional tests of the sensors with cyclic switch-off of the sensor outputs for max. 0.25 ms. Short-circuit recognition by the evaluation is not necessary.
Schmersal Canada Ltd., 29 Centennial Road, Unit 1, Orangeville, Ontario L9W 1R1 Canada
The details and data referred to have been carefully checked. Images may diverge from original. Further technical data can be found in the manual. Technical amendments and errors possible.
Generated on: 2024-05-11, 8:52 p.m.