## Worksheet
PSC1-E-131-12DI-10DIO
Expansion module for the product series PSC1-C-100 12 digital safe inputs 10 switchable safe inputs/outputs 2 additional signalling outputs
Ordering data
Product type description | PSC1-E-131-12DI-10DIO
Article number (order number) | 103011953
EAN (European Article Number) | 4030661480886
eCl@ss number, version 12.0 | 27-24-22-07
eCl@ss number, version 11.0 | 27-24-22-07
eCl@ss number, version 9.0 | 27-24-22-07
ETIM number, version 7.0 | EC000236
ETIM number, version 6.0 | EC000236
General data
Gross weight | 400 g
General data - Features
Number of digital fail-safe inputs | 12
Number of digital fail-safe in-/outputs | 10
Number of signalling outputs | 2
<table><tr><td>Safety classification</td></tr></table>
Performance Level, up to | e
Category | 4
Safety Integrity Level (SIL), suitable for applications in | 3
Mission time | 20 Year(s)
Mechanical data
Mounting | can be clipped into standard rail
Mechanical data - Connection technique
Cable section, minimum | 0.2 mm²
Cable section, maximum | 2.5 mm²
Wire cross-section, minimum | 24 AWG
Wire cross-section, maximum | 12 AWG
Terminal (mechanical) | Removable screw terminals
Mechanical data - Dimensions
Width | 45 mm
Height | 100 mm
Depth | 115 mm
Ambient conditions
Degree of protection | IP20
Ambient temperature | +0 ... +50 °C
Storage and transport temperature | -25 ... +70 °C
Relative humidity, minimum | 5 %
Relative humidity, maximum | 85 %
Note (Relative humidity) | non-condensing
Permissible installation altitude above sea level, maximum | 2,000 m
Ambient conditions - Insulation values
Overvoltage category | III
Degree of pollution | 2
Electrical data
Operating voltage | 24 VDC -15 % / +20 %
Rated operating voltage | 24 VDC
Electrical data - Safety digital outputs
Rated operating current (safety outputs) | 2,000 mA
Electrical data - Safe relay outputs
Voltage, Utilisation category AC-15 | 230 VAC
Current, Utilisation category AC-15 | 2 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 2 A
Electrical data - Electromagnetic compatibility (EMC)
Electromagnetic compatibility | DIN EN 62061 DIN EN 61800-3
Interfering radiation | DIN EN 61000-6-4
EMC rating | DIN EN 61000-6-7 DIN EN 61326-3 DIN EN 61000-6-2
Scope of delivery
Scope of delivery | Backplane bus connector Connector terminals
Schmersal Ltd., Sparrowhawk Close, WR14 1GL Malvern
The details and data referred to have been carefully checked. Images may diverge from original. Further technical data can be found in the manual. Technical amendments and errors possible.
Generated on: 18/10/2025, 10:01