## Worksheet
RSS 36-D-ST
| Universal coding with RFID technology 1 x connector socket M12, 8-pole Actuation from side Thermoplastic enclosure RFID-technology for needs-based protection against tampering | Misaligned actuation possible 27 mm x 108.2 mm x 35 mm High repeat accuracy of the switching points 2 short-circuit proof PNP safety outputs Integral cross-short, wire-breakage and external voltage monitoring of the safety cables up to the control cabinet
Ordering data
Product type description | RSS 36-D-ST
Article number (order number) | 101213954
EAN (European Article Number) | 4030661410623
eCl@ss number, version 12.0 | 27-27-46-01
eCl@ss number, version 11.0 | 27-27-24-03
eCl@ss number, version 9.0 | 27-27-24-03
ETIM number, version 7.0 | EC001829
ETIM number, version 6.0 | EC001829
Approvals - Standards
Certificates | TÜV cULus ECOLAB FCC IC ANATEL
General data
Standards | EN ISO 13849-1 EN IEC 60947-5-3 EN IEC 61508
Coding | Universal coding
Coding level according to EN ISO 14119 | Low
Working principle | RFID
Frequency band RFID | 125 kHz
Transmitter output RFID, maximum | -6 dB/m
Housing construction form | Block
Installation conditions (mechanical) | not flush
Sensor topology | Sensor for series wiring
Housing material | Glass-fibre, reinforced thermoplastic
Reaction time, maximum | 100 ms
Duration of risk, maximum | 200 ms
Reaction time, switching off safety outputs via actuator, maximum | 100 ms
Reaction time, switching off safety outputs via safety inputs, maximum | 0.5 ms
Gross weight | 80 g
General data - Features
Diagnostic output | Yes
Short circuit detection | Yes
Cross-circuit detection | Yes
Series-wiring | Yes
Safety functions | Yes
Cascadable | Yes
Integral system diagnostics, status | Yes
Number of LEDs | 3
Number of semi-conductor outputs with signaling function | 1
Number of fail-safe digital outputs | 2
<table><tr><td>Safety classification</td></tr></table>
Standards | EN ISO 13849-1 EN IEC 61508
Performance Level, up to | e
Category | 4
PFH value | 2.70 x 10⁻¹⁰ /h
PFD value | 2.10 x 10⁻⁵
Safety Integrity Level (SIL), suitable for applications in | 3
Mission time | 20 Year(s)
Mechanical data
Actuating panels | lateral
Active area | lateral
Mechanical life, minimum | 1,000,000 Operations
Note (Mechanical life) | Actuating speed < 0.25 m/s Operations for door weights ≤ 5 kg
Mounting | A screw length of 25 mm is sufficient for sensor mounting and for side mounting of the actuators. 30 mm long screws are recommended when the actuator is mounted upright and/or when the sealing discs are used.
Type of the fixing screws | 2x M4 (cylinder head screws with washers DIN 125A / form A)
Tightening torque of the fixing screws, minimum | 2.2 Nm
Tightening torque of the fixing screws, maximum | 2.5 Nm
Mechanical data - Switching distances according EN IEC 60947-5-3
Switch distance, typical | 12 mm
Assured switching distance &quot;ON&quot; Sao | 10 mm
Assured switching distance &quot;OFF&quot; Sar | 20 mm
Hysteresis (Switching distance), maximum | 2 mm
Repeat accuracy R | 0.5 mm
Note (Repeat accuracy R) | Axial offset: The long side allows for a maximum height misalignment (x) of sensor and actuator of 8 mm (e.g. mounting tolerance or due to guard door sagging). The axial misalignment (y) is max. ± 18 mm (see figure: Operating principle).Minimum clearance between two sensor systems 100 mm.
Mechanical data - Connection technique
Note (length of the sensor chain) | Cable length and cross-section change the voltage drop dependiing on the output current
Note (series-wiring) | Unlimited number of devices, oberserve external line fusing, max. 31 devices in case of serial diagnostic SD
Termination | Connector M12, 8-pole
Mechanical data - Dimensions
Length of sensor | 22 mm
Width of sensor | 106.3 mm
Height of sensor | 25 mm
Ambient conditions
Degree of protection | IP65 IP67 IP69
Ambient temperature | -28 ... +70 °C
Storage and transport temperature | -28 ... +85 °C
Relative humidity, maximum | 93 %
Note (Relative humidity) | non-condensing non-icing
Resistance to vibrations | 10 … 55 Hz, amplitude 1 mm
Restistance to shock | 30 g / 11 ms
Protection class | III
Permissible installation altitude above sea level, maximum | 2,000 m
Ambient conditions - Insulation values
Rated insulation voltage Ui | 32 VDC
Rated impulse withstand voltage Uimp | 0.8 kV
Overvoltage category | III
Degree of pollution | 3
Electrical data
Operating voltage | 24 VDC -15 % / +10 % (stabilised PELV power supply)
Operating current, minimum | 0.5 mA
No-load supply current I0, typical | 35 mA
Rated operating voltage | 24 VDC
Operating current | 600 mA
Required rated short-circuit current | 100 A
Time to readiness, maximum | 2,000 ms
Switching frequency, maximum | 1 Hz
Utilisation category DC-12 | 24 VDC / 0.05 A
Electrical fuse rating, maximum | 2 A
Electrical data - Safety digital inputs
Designation, Safety inputs | X1 and X2
Current consumption of the safety inputs | 5 mA
Test pulse duration, maximum | 1 ms
Test pulse interval, minimum | 100 ms
Classification ZVEI CB24I, Sink | C1
Classification ZVEI CB24I, Source | C1 C2 C3
Electrical data - Safety digital outputs
Designation, Safety outputs | Y1 and Y2
Rated operating current (safety outputs) | 250 mA
Output current, (fail-safe output), maximum | 0.25 A
Design of control elements | short-circuit proof, p-type
Voltage drop Ud, maximum | 1 V
Leakage current Ir, maximum | 0.5 mA
Voltage, Utilisation category DC-12 | 24 VDC
Current, Utilisation category DC-12 | 0.25 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 0.25 A
Test pulse interval, typical | 1000 ms
Test pulse duration, maximum | 0.3 ms
Classification ZVEI CB24I, Source | C2
Classification ZVEI CB24I, Sink | C1 C2
Electrical data - Diagnostic outputs
Designation, Diagnostic outputs | OUT
Design of control elements | short-circuit proof, p-type
Voltage drop Ud, maximum | 2 V
Voltage, Utilisation category DC-12 | 24 VDC
Current, Utilisation category DC-12 | 0.05 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 0.05 A
Electrical data - Electromagnetic compatibility (EMC)
Interfering radiation | IEC 61000-6-4
Status indication
Note (LED switching conditions display) | LED yellow: Operating condition LED green: Supply voltage LED red: Fault
Pin assignment
PIN 1 | 1A1 Ue: (1)
PIN 2 | X1 Safety input 1
PIN 3 | A2 GND Blue
PIN 4 | Y1 Safety output 1 Black
PIN 5 | OUT Diagnostic output OUT Grey
PIN 6 | X2 Safety input 2 violet
PIN 7 | Y2 Safety output 2 red
PIN 8 | IN without function Pink
Scope of delivery
Scope of delivery | Actuator must be ordered separately.
Accessory
Recommendation (actuator) | RST 36-1 RST 36-1-R
Recommended safety switchgear | PROTECT PSC1 SRB-E-301ST SRB-E-201LC
Note
Note (General) | Evaluation requirements: dual-channel safety input, suitable for p-type sensors with NO function. The safety-monitoring module must tolerate internal functional tests of the sensors with cyclic switch-off of the sensor outputs for max. 0.5 ms. Short-circuit recognition by the evaluation is not necessary.
Schmersal Ltd., Sparrowhawk Close, WR14 1GL Malvern
The details and data referred to have been carefully checked. Images may diverge from original. Further technical data can be found in the manual. Technical amendments and errors possible.
Generated on: 17/01/2025, 22:52