## Worksheet
CSP 11-34F2-D-M-ST
| 1 x connector plug M12, 8-pole Actuation from side with On-site acknowledgment NOTICE: Not available! (Replacement: RSS 36 I) Thermoplastic enclosure Electronic contact-free, coded system | Tampering protection by paired coding of sensor and actuator Misaligned actuation possible High repeat accuracy of the switching points Max. length of the sensor chain 200 m 2 short-circuit proof PNP safety outputs Integral cross-short, wire-breakage and external voltage monitoring of the safety cables up to the control cabinet
Ordering data
Note (Delivery capacity) | Not available!
Product type description | CSP 11-34F2-D-M-ST
Article number (order number) | 101208005
EAN (European Article Number) | 4030661382029
eCl@ss number, version 12.0 | 27-27-26-06
eCl@ss number, version 11.0 | 27-27-24-04
eCl@ss number, version 9.0 | 27-27-24-04
ETIM number, version 7.0 | EC001487
ETIM number, version 6.0 | EC001487
Approvals - Standards
Certificates | cULus
General data
Standards | EN ISO 13849-1 EN IEC 60947-5-3 EN IEC 61508
Working principle | inductive
Housing construction form | Block
Installation conditions (mechanical) | not flush
Sensor topology | Sensor for series wiring
Housing material | Glass-fibre, reinforced thermoplastic
Active area | Glass-fibre, reinforced thermoplastic
Reaction time, maximum | 30 ms
Duration of risk, maximum | 60 ms
Gross weight | 140 g
General data - Features
Diagnostic output | Yes
Short circuit detection | Yes
Cross-circuit detection | Yes
Safety functions | Yes
Cascadable | Yes
Input for reset pushbutton, with edge monitoring | Yes
Input for enabling pushbutton, suitable for automatic start | Yes
On-site acknowledgment | Yes
Integral system diagnostics, status | Yes
Number of LEDs | 3
Number of semi-conductor outputs with signaling function | 1
Number of fail-safe digital outputs | 2
Number of series-wiring of sensors | 31
<table><tr><td>Safety classification</td></tr></table>
Vorschriften | EN IEC 60947-5-3 EN IEC 61508
Performance Level, up to | e
Category | 4
PFH value | 3.60 x 10⁻⁹ /h
Safety Integrity Level (SIL), suitable for applications in | 3
Mission time | 20 Year(s)
Mechanical data
Actuating panels | lateral
Active area | lateral
Mechanical data - Switching distances according EN IEC 60947-5-3
Switch distance, typical | 11 mm
Assured switching distance &quot;ON&quot; Sao | 8 mm
Assured switching distance &quot;OFF&quot; Sar | 15 mm
Hysteresis (Switching distance), maximum | 1.5 mm
Repeat accuracy R | 0.5 mm
Note (Repeat accuracy R) | Axial offset: The long side allows for a maximum height misalignment (x) of sensor and actuator of 30 mm (e.g. mounting tolerance or due to guard door sagging). The axial misalignment (y) is max. ± 8 mm.
Mechanical data - Connection technique
Note (length of the sensor chain) | Cable length and cross-section change the voltage drop dependiing on the output current
Termination | Connector plug M12, 8-pole
Mechanical data - Dimensions
Length of sensor | 27 mm
Width of sensor | 35 mm
Height of sensor | 108.2 mm
Ambient conditions
Degree of protection | IP65 IP67
Ambient temperature | -25 ... +70 °C
Storage and transport temperature | -25 ... +85 °C
Resistance to vibrations | 10 … 55 Hz, amplitude 1 mm
Restistance to shock | 30 g / 11 ms
Protection class | II
Ambient conditions - Insulation values
Rated insulation voltage Ui | 32 VAC/DC
Rated impulse withstand voltage Uimp | 0.8 kV
Overvoltage category | III
Degree of pollution | 3
Electrical data
Operating voltage | 24 VDC -15 % / +10 %
No-load supply current I0, typical | 100 mA
Rated operating voltage | 24 VDC
Operating current | 600 mA
Required rated short-circuit current | 100 A
Utilisation category DC-12 | 24 VDC
Utilisation category DC-12 | 0.05 A
Utilisation category DC-13 | 24 VDC
Utilisation category DC-13 | 0.05 A
Note (Electrical data, Fuse rating) | (Circuit breaker)
Switching frequency, approx. | 3 Hz
Utilisation category DC-12 | 24 VDC / 0.05 A
Electrical fuse rating, maximum | 2 A
Electrical data - Safety digital outputs
Rated operating current (safety outputs) | 250 mA
Output current, (fail-safe output), maximum | 0.25 A
Design of control elements | p-type
Voltage drop Ud, maximum | 0.5 V
Leakage current Ir, maximum | 0.5 mA
Voltage, Utilisation category DC-12 | 24 VDC
Current, Utilisation category DC-12 | 0.25 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 0.25 A
Electrical data - Digital Output
Design of control elements | p-type
Electrical data - Diagnostic outputs
Operating current | 50 mA
Voltage drop Ud, maximum | 5 V
Voltage, Utilisation category DC-12 | 24 VDC
Current, Utilisation category DC-12 | 0.05 A
Electrical data - Electromagnetic compatibility (EMC)
Interfering radiation | IEC 61000-6-4
EMC rating | IEC 61000-6-2
Pin assignment
PIN 1 | 1A1 Ue: (1)
PIN 2 | X1 Safety input 1
PIN 3 | A2 GND
PIN 4 | Y1 Safety output 1
PIN 5 | OUT Diagnostic output OUT
PIN 6 | X2 Safety input 2
PIN 7 | Y2 Safety output 2
PIN 8 | IN On-site acknowledgment
Scope of delivery
Scope of delivery | Actuator must be ordered separately.
Accessory
Recommendation (actuator) | CSP 34-S-1
Recommended safety switchgear | PROTECT PSC1 SRB-E-301ST SRB-E-201LC
Note
Note (General) | When safety gate monitoring by the safety sensor CSP 34F2 is required, an acknowledge button should be positioned so that the danger area can be viewed. When the button is pushed, a 24 VDC signal is generated at the reset input of the CSP 34F2. If the gate is closed the safety outputs are released with the negative signal edge. After the gate is opened it needs to be acknowledge before it can be released again. On-site acknowledgment
Schmersal Ltd., Sparrowhawk Close, WR14 1GL Malvern
The details and data referred to have been carefully checked. Images may diverge from original. Further technical data can be found in the manual. Technical amendments and errors possible.
Generated on: 23/03/2025, 00:04