## Worksheet
AES 1112.3 24 VAC
Monitoring of BNS range magnetic safety sensors 1 safety contact, STOP 0
Ordering data
Product type description | AES 1112.3 24 VAC
Article number (order number) | 101128800
EAN (European Article Number) | 4030661059198
eCl@ss number, version 12.0 | 27-37-18-19
eCl@ss number, version 11.0 | 27-37-18-19
eCl@ss number, version 9.0 | 27-37-18-19
ETIM number, version 7.0 | EC001449
ETIM number, version 6.0 | EC001449
Approvals - Standards
Certificates | cULus
General data
Standards | BG-GS-ET-14 BG-GS-ET-20 EN IEC 62061 EN ISO 13849-1 EN IEC 60947-5-1 EN IEC 60947-5-3 EN IEC 60947-5-5 EN IEC 60204-1 EN IEC 60947-1
Climatic stress | EN 60068-2-3 BG-GS-ET-14
Housing material | Glass-fibre reinforced thermoplastic, ventilated
Gross weight | 120 g
General data - Features
Wire breakage detection | Yes
Automatic reset function | Yes
Reset after disconnection of supply voltage | Yes
Integral system diagnostics, status | Yes
Number of LEDs | 1
Number of normally closed (NC) | 2
Number of normally open (NO) | 1
Number of safety contacts | 1
<table><tr><td>Safety classification</td></tr></table>
Standards | EN ISO 13849-1 EN IEC 61508
Stop-Category | 0
<table><tr><td>Safety classification - Relay outputs</td></tr></table>
Performance Level, up to | c
Category | 1
PFH value | 1.14 x 10⁻⁶ /h
Notice | for max. 50,000 switching cycles/year and max. 80% contact load
Safety Integrity Level (SIL), suitable for applications in | 1
Mission time | 20 Year(s)
Mechanical data
Mechanical lifetime, minimum | 10,000,000 Operations
Mounting | Snaps onto standard DIN rail to EN 60715
Mechanical data - Connection technique
Terminal designations | IEC/EN 60947-1
Cable section, maximum | 2.5 mm²
Tightening torque of Clips | 0.6 Nm
Allowed type of cable | solid single-wire flexible
Terminal (mechanical) | Schraubklemmen
Mechanical data - Dimensions
Width | 22.5 mm
Height | 75 mm
Depth | 110 mm
Ambient conditions
Degree of protection of the enclosure | IP40
Degree of protection of the installation space | IP54
Degree of protection of clips or terminals | IP20
Ambient temperature | +0 ... +55 °C
Storage and transport temperature | -25 ... +70 °C
Resistance to vibrations | 10...55 Hz, Amplitude 0.35 mm, ± 15 %
Restistance to shock | 30 g / 11 ms
Ambient conditions - Insulation values
Rated impulse withstand voltage Uimp | 4 kV
Overvoltage category | III
Degree of pollution | 2
Electrical data
Frequency range | 50 Hz 60 Hz
Thermal test current | 4 A
Rated operating voltage | 24 VAC
Rated AC voltage for controls, 50 Hz, minimum | 20.4 VAC
Rated control voltage at AC 50 Hz, maximum | 26.4 VAC
Rated AC voltage for controls, 60 Hz, minimum | 20.4 VAC
Rated control voltage at AC 60 Hz, maximum | 26.4 VAC
Electrical power consumption | 2.4 W
Contact resistance, maximum | 0.1 Ω
Note (Contact resistance) | in new state
Drop-out delay in case of power failure, typically | 80 ms
Drop-out delay in case of emergency, typically | 20 ms
Pull-in delay at automatic start, maximum, typically | 100 ms
Pull-in delay at RESET, typically | 20 ms
Material of the contacts, electrical | AgCdO
Electrical data - Safe relay outputs
Voltage, Utilisation category AC-15 | 230 VAC
Current, Utilisation category AC-15 | 3 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 2 A
Switching capacity, minimum | 10 VDC
Switching capacity, minimum | 10 mA
Switching capacity, maximum | 250 VAC
Switching capacity, maximum | 8 A
Electrical data - Digital inputs
Conduction resistance, maximum | 40 Ω
Electrical data - Digital Output
Voltage, Utilisation category DC-12 | 24 VDC
Current, Utilisation category DC-12 | 0.1 A
Electrical data - Relay outputs (auxiliary contacts)
Switching capacity, maximum | 24 VDC
Switching capacity, maximum | 2 A
Electrical data - Electromagnetic compatibility (EMC)
EMC rating | EMC-Directive
Status indication
Indicated operating states | Authorised operation
Other data
Note (applications) | Safety sensor Guard system
Note
Note (General) | Inductive loads (e.g. contactors, relays, etc.) are to be suppressed by means of a suitable circuit.
Wiring example
Note (Wiring diagram) | The wiring diagram is shown with guard doors closed and in de-energised condition. To secure 2 guard doors up to PL c and Category 1 Monitoring 2 guard door(s), each with a magnetic safety sensor of the BNS range Monitoring one guard door: If only one magnetic safety sensor is connected to S1, the terminals S22, S32 and C of S2 must be bridged.
Schmersal Ltd., Sparrowhawk Close, WR14 1GL Malvern
The details and data referred to have been carefully checked. Images may diverge from original. Further technical data can be found in the manual. Technical amendments and errors possible.
Generated on: 22/10/2025, 00:23