## Worksheet
SRB-E-301MC-CC
| Plug-in spring-cage terminal blocks with coding 1 Signalling contact Suitable for applications up to Cat. 4 / PL e und up to SIL 3 1 or 2 channel signal evaluation | Start / feedback circuit monitoring Optionally with short-circuit recognition 3 safety contacts, stop category 0
Ordering data
Product type description | SRB-E-301MC-CC
Article number (order number) | 103016932
EAN (European Article Number) | 4030661511603
eCl@ss number, version 12.0 | 27-37-18-19
eCl@ss number, version 11.0 | 27-37-18-19
eCl@ss number, version 9.0 | 27-37-18-19
ETIM number, version 7.0 | EC001449
ETIM number, version 6.0 | EC001449
General data
Standards | EN IEC 62061 EN ISO 13849-1 EN IEC 60947-5-1 EN IEC 60947-5-3 EN IEC 60947-5-5 EN IEC 61508 EN IEC 60204-1 EN IEC 60947-1
Climatic stress | EN 60068-2-78
Housing material | Glass-fibre reinforced thermoplastic, ventilated
Gross weight | 250 g
General data - Features
Electronic Fuse | Yes
Wire breakage detection | Yes
Cross-circuit detection | Yes
Removable Terminals | Yes
Start input | Yes
Feedback circuit | Yes
Automatic reset function | Yes
Earth connection detection | Yes
Integral system diagnostics, status | Yes
Number of auxiliary contacts | 1
Number of LEDs | 5
Number of normally closed (NC) | 2
Number of Safety contacts, STOP 0 | 3
<table><tr><td>Safety classification</td></tr></table>
Standards | EN ISO 13849-1 EN IEC 62061 EN IEC 61508
Stop-Category | 0
<table><tr><td>Safety classification - Relay outputs</td></tr></table>
Performance Level, up to | e
Category | 4
Diagnostic Coverage (DC) Level | &gt; 99 %
PFH value | 6.00 x 10⁻⁹ /h
PFD value | 4.00 x 10⁻⁵
Safety Integrity Level (SIL), suitable for applications in | 3
Mission time | 20 Year(s)
Common Cause Failure (CCF), minimum | 65
Mechanical data
Mechanical life, minimum | 10,000,000 Operations
Mounting | Snaps onto standard DIN rails to IEC 60715
Mechanical data - Connection technique
Terminal designations | IEC 60947-1
Termination | Cage clamp, plug-in rigid or flexible
Cable section, minimum | 0.25 mm²
Cable section, maximum | 1.5 mm²
Mechanical data - Dimensions
Width | 22.5 mm
Height | 98 mm
Depth | 115 mm
Ambient conditions
Degree of protection of the enclosure | IP40
Degree of protection of the mounting space | IP54
Degree of protection of clips or terminals | IP20
Ambient temperature | -25 ... +60 °C
Storage and transport temperature | -40 ... +85 °C
Resistance to vibrations | 10 ... 55 Hz, Amplitude 0.35 mm
Restistance to shock | 30 g / 11 ms
Ambient conditions - Insulation values
Rated impulse withstand voltage Uimp | 4 kV
Overvoltage category | III
Degree of pollution | 2
Electrical data
Frequency range | 50 Hz 60 Hz
Operating voltage | 24 VAC -15 % / +10 %24 VDC -15 % / +20 %
Ripple voltage | 10 %
Rated operating voltage | 24 VAC
Rated operating voltage | 24 VDC
Rated AC voltage for controls, 50 Hz, minimum | 20.4 VAC
Rated control voltage at AC 50 Hz, maximum | 26.4 VAC
Rated AC voltage for controls, 60 Hz, minimum | 20.4 VAC
Rated control voltage at AC 60 Hz, maximum | 26.4 VAC
Rated AC voltage for controls at DC minimum | 20.4 VDC
Rated control voltage at DC, maximum | 28.8 VDC
Electrical power consumption | 2.9 W
Electrical power consumption | 5 VA
Contact resistance, maximum | 0.1 Ω
Note (Contact resistance) | in new state
Drop-out delay in case of power failure, typically | 80 ms
Drop-out delay in case of emergency, typically | 20 ms
Pull-in delay at automatic start, maximum, typically | 100 ms
Pull-in delay at RESET, typically | 20 ms
Switching frequency, maximum | 0.3 Hz
Material of the contacts, electrical | Ag-Ni, self-cleaning, positive drive
Electrical data - Safe relay outputs
Voltage, Utilisation category AC-15 | 230 VAC
Current, Utilisation category AC-15 | 4 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 4 A
Switching capacity, minimum | 10 VDC
Switching capacity, minimum | 10 mA
Switching capacity, maximum | 250 VAC
Switching capacity, maximum | 6 A
Electrical data - Digital inputs
Conduction resistance, maximum | 40 Ω
Electrical data - Relay outputs (auxiliary contacts)
Switching capacity, maximum | 24 VDC
Switching capacity, maximum | 1 A
Electrical data - Electromagnetic compatibility (EMC)
EMC rating | EMC-Directive
Status indication
Indicated operating states | Position relay K2 Position relay K1 Internal operating voltage Ui UB: Supply voltage on
Other data
Note (applications) | Safety sensor Guard system hinged safety guard Emergency-Stop button Pull-wire emergency stop switches Safety light curtain Safety light barriers
Schmersal India Pvt. Ltd., Plot No - G-7/1, Ranjangaon MIDC, Tal. - Shirur, Dist.- Pune 412 220
The details and data referred to have been carefully checked. Images may diverge from original. Further technical data can be found in the manual. Technical amendments and errors possible.
Generated on: 22/05/2024, 1:59 am