## Worksheet
BN 650-10Z
| With pre-wired cable Actuation from side with bias magnet Non-contact principle Long life | Actuating surface and direction of actuation marked by switch symbol Construction form Ø 13 mm Thermoplastic enclosure Actuating distance up to 60 mm depending on actuating magnet and version with central mounting
Ordering data
Note (Delivery capacity) | Not available!
Product type description | BN 650-10Z
Article number (order number) | 101187273
EAN (European Article Number) | 4030661335728
eCl@ss number, version 12.0 | 27-27-43-02
eCl@ss number, version 11.0 | 27-27-01-05
eCl@ss number, version 9.0 | 27-27-01-05
ETIM number, version 7.0 | EC002544
ETIM number, version 6.0 | EC002544
General data
Working principle | Magnetic drive
Housing construction form | Cylinder smooth
Housing material | Glass-fibre, reinforced thermoplastic
Gross weight | 65 g
General data - Features
Suitable for elevators | Yes
bias magnet | Yes
Number of normally open (NO) | 1
Mechanical data
Actuating panels | lateral
Actuating element | Magnet
Mechanical life, minimum | 1,000,000,000 Operations
Actuating speed, maximum | 18 m/s
Mounting | central with threated flange
Tightening torque of nuts, maximum | 3 Nm
Mechanical data - Switching distances according EN IEC 60947-5-3
Switching distance Sn | 5 mm … 50 mm BP 10 = 5 mm 2 x BP 10 = 17 mm BP 15 = 6 mm 2 x BP 15 = 17 mm 2 x BP 15/2 = 17 mm BP 34 = 15 ... 20 mm BP 20 = 20 mm BP 31 = 20 mm BP 11 = 20 mm BP 12 = 10 ... 30 mm BP 21 = 25 ... 50 mm
Note (Switching distance Sn) | Actuating distance up to 50 mm depending on actuating magnet and version. The specified switching distances are applicable for the actuation of individually mounted components without ferromagnetic influence. A change of the distance, either positive or negative, is possible due to ferromagnetic influences. The mutual interference between multiple actuating magnets must be observed.
Repeat accuracy R | 0.3 mm
Mechanical data - Connection technique
Length of cable | 1 m
Termination | Cable
Wire cross-section | 0.25 mm2
Wire cross-section | 23 AWG
Material of the Cable mantle | H03VV-F
Mechanical data - Dimensions
Diameter of sensor | 13 mm
width across flats | 22 BK
Length of sensor | 103 mm
Ambient conditions
Degree of protection | IP67
Ambient temperature | -25 ... +75 °C
Resistance to vibrations | 10 … 55 Hz, amplitude 1 mm
Restistance to shock | 30 g, on sine wave oscillation
Resistant to vibration | 30 g, on sine wave oscillation
Electrical data
Switching voltage, maximum | 200 VAC
Switching voltage, maximum | 200 VDC
Switching current, maximum | 1 A
Switching capacity, maximum | 30 W
Switching capacity, maximum | 30 VA
Switching element | Normally open contact (NO)
Bounce duration, minimum | 0.3 ms
Bounce duration, maximum | 0.2 ms
Switching frequency, maximum | 300 Hz
Maximale Schalthäufigkeit | 1,080,000 /h
Electrical data - Digital Output
Design of control elements | Reed contacts
Scope of delivery
Scope of delivery | Actuator must be ordered separately.
Accessory
Recommendation (actuator) | BP 10 2x BP 10 BP 15 2x BP 15 2x BP 15/2 BP 34 BP 20 BP 31 BP 11 BP 12 BP 21
Recommendation (actuator, lift switchgear) | BP 10 2 x BP 15/2 2 x BP 15 2 x BP 10 BP 15 BP 34
Schmersal India Pvt. Ltd., Plot No - G-7/1, Ranjangaon MIDC, Tal. - Shirur, Dist.- Pune 412 220
The details and data referred to have been carefully checked. Images may diverge from original. Further technical data can be found in the manual. Technical amendments and errors possible.
Generated on: 01/04/2025, 2:44 pm