## Worksheet
PROTECT-IE-11
Input for up to 4 sensors per interface e.g.: magnetic safety switches type BNS, emergency stop devices, interlocking devices and others 2 safety contacts
Ordering data
Product type description | PROTECT-IE-11
Article number (order number) | 101182805
EAN (European Article Number) | 4250116202133
eCl@ss number, version 12.0 | 27-37-18-19
eCl@ss number, version 11.0 | 27-37-18-19
eCl@ss number, version 9.0 | 27-37-18-19
ETIM number, version 7.0 | EC001449
ETIM number, version 6.0 | EC001449
Available until | 31.12.2024
Approvals - Standards
Certificates | cULus
General data
Standards | EN IEC 62061 EN ISO 13849-1 EN IEC 60947-5-1 EN IEC 60947-5-3 EN IEC 60947-5-5 EN IEC 61508 EN IEC 60204-1 EN IEC 60947-1
Climatic stress | EN 60068-2-78
Housing material | Glass-fibre reinforced thermoplastic, ventilated
Gross weight | 140 g
General data - Features
Electronic Fuse | Yes
Wire breakage detection | Yes
Cross-circuit detection | Yes
Automatic reset function | Yes
Earth connection detection | Yes
Integral system diagnostics, general | Yes
Number of auxiliary contacts | 1
Number of LEDs | 5
Number of normally closed (NC) | 1
Number of normally open (NO) | 1
Number of safety contacts | 2
<table><tr><td>Safety classification</td></tr></table>
Standards | EN IEC 60947-5-1 EN IEC 61508
Stop-Category | 0
<table><tr><td>Safety classification - Relay outputs</td></tr></table>
Performance Level, up to | d
Category | 3
Diagnostic Coverage (DC) Level | 60 %
PFH value | 2.00 x 10⁻⁷ /h
Notice | for max. 36,500 switching cycles/year and max. 60% contact load
Safety Integrity Level (SIL), suitable for applications in | 2
Mission time | 20 Year(s)
Common Cause Failure (CCF), minimum | 65
Mechanical data
Mechanical life, minimum | 10,000,000 Operations
Mounting | Snaps onto standard DIN rail to EN 60715
Mechanical data - Connection technique
Terminal designations | IEC/EN 60947-1
Termination | Cage clamps
Cable section, minimum | 0.2 mm²
Cable section, maximum | 2.5 mm²
Mechanical data - Dimensions
Width | 48 mm
Height | 126 mm
Depth | 61 mm
Ambient conditions
Degree of protection of the enclosure | IP20
Degree of protection of the mounting space | IP20
Degree of protection of clips or terminals | IP20
Ambient temperature | -25 ... +55 °C
Storage and transport temperature | -40 ... +85 °C
Resistance to vibrations | 10...55 Hz, Amplitude 0.35 mm, ± 15 %
Restistance to shock | 30 g / 11 ms
Ambient conditions - Insulation values
Rated impulse withstand voltage Uimp | 0.8 kV
Overvoltage category | III
Degree of pollution | 2
Electrical data
Operating voltage | 24 VDC -15 % / +20 %
Ripple voltage | 10 %
Rated operating voltage | 24 VDC
Rated AC voltage for controls at DC minimum | 20.4 VDC
Rated control voltage at DC, maximum | 28.8 VDC
Electrical power consumption | 1.7 W
Input resistance at Ue | 2,900 Ω
Contact resistance, maximum | 0.1 Ω
Note (Contact resistance) | in new state
Drop-out delay in case of &quot;emergency stop&quot;, maximum | 20 ms
Pull-in delay at automatic start, maximum | 20 ms
Electrical data - Safe relay outputs
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 2 A
Switching capacity, minimum | 10 VDC
Switching capacity, minimum | 10 mA
Switching capacity, maximum | 24 VAC
Switching capacity, maximum | 2 A
Electrical data - Digital inputs
Input signal, HIGH Signal &quot;1&quot; | 19 - 28,8 VDC
Input signal, LOW Signal &quot;0&quot; | 0 - 1 VDC
Conduction resistance, maximum | 40 Ω
Electrical data - Digital Output
Voltage, Utilisation category DC-12 | 24 VDC
Current, Utilisation category DC-12 | 0.1 A
Electrical data - Relay outputs (auxiliary contacts)
Switching capacity, maximum | 24 VDC
Switching capacity, maximum | 0.1 A
Electrical data - Electromagnetic compatibility (EMC)
EMC rating | EMC-Directive
Status indication
Indicated operating states | Position relay K2 Position relay K1 Position relay K3 Position relay K3
Other data
Note (applications) | Safety sensor Guard system Emergency-Stop button Pull-wire emergency stop switches
Schmersal India Pvt. Ltd., Plot No - G-7/1, Ranjangaon MIDC, Tal. - Shirur, Dist.- Pune 412 220
The details and data referred to have been carefully checked. Images may diverge from original. Further technical data can be found in the manual. Technical amendments and errors possible.
Generated on: 20/05/2024, 11:20 pm