## Worksheet
SRB202CS 24VDC
Level 1: Reset without edge detection, Optional Automatic reset function, Level 2: / Opener (NC) Opener (NC) Two-functions safety monitoring module (double evaluation) 2 enabling paths with different shut-down behaviour, e.g. emergency exit opens both enabling paths (level 1); guard door monitoring only opens the second enabling path (level 2) Suitable for signal processing of potential-free contacts, e.g. Emergency Stop command devices (level 1), position switches with safety function, solenoid interlocks and safety sensors (level 2) 2 Signalling outputs
Ordering data
Replacement article number | 101177154
Product type description | SRB202CS 24VDC
Article number (order number) | 101176208
EAN (European Article Number) | 4250116201914
eCl@ss number, version 12.0 | 27-37-18-19
eCl@ss number, version 11.0 | 27-37-18-19
eCl@ss number, version 9.0 | 27-37-18-19
ETIM number, version 7.0 | EC001449
ETIM number, version 6.0 | EC001449
Available until | 31.12.2024
Approvals - Standards
Certificates | cULus
General data
Standards | EN IEC 62061 EN ISO 13849-1 EN IEC 60947-5-1 EN IEC 60947-5-3 EN IEC 60947-5-5 EN IEC 61508 EN IEC 60204-1 EN IEC 60947-1
Climatic stress | EN 60068-2-78
Housing material | Glass-fibre reinforced thermoplastic, ventilated
Gross weight | 235 g
General data - Features
Electronic Fuse | Yes
Wire breakage detection | Yes
Removable Terminals | Yes
Start input | Yes
Feedback circuit | Yes
Automatic reset function | Yes
Earth connection detection | Yes
Integral system diagnostics, status | Yes
Number of auxiliary contacts | 2
Number of inputs for NC | 2
Number of inputs for NO | 2
Number of LEDs | 6
Number of safety contacts | 2
<table><tr><td>Safety classification</td></tr></table>
Standards | EN IEC 60947-5-1 EN IEC 61508
Stop-Category | 0
<table><tr><td>Safety classification - Relay outputs</td></tr></table>
Performance Level, stop 0, up to | e
Category, Stop 0 | 4
Diagnostic Coverage (DC) Level, Stop 0 | ≥ 99 %
PFH value, Stop 0 | 2.00 x 10⁻⁸ /h
Safety Integrity Level (SIL), Stop 0, suitable for applications in | 3
Mission time | 20 Year(s)
Common Cause Failure (CCF), minimum | 65
Mechanical data
Mechanical life, minimum | 10,000,000 Operations
Mounting | Snaps onto standard DIN rail to EN 60715
Mechanical data - Connection technique
Terminal designations | IEC/EN 60947-1
Termination | rigid or flexible Screw terminals M20 x 1.5
Cable section, minimum | 0.25 mm²
Cable section, maximum | 2.5 mm²
Tightening torque of Clips | 0.6 Nm
Mechanical data - Dimensions
Width | 22.5 mm
Height | 100 mm
Depth | 121 mm
Ambient conditions
Degree of protection of the enclosure | IP40
Degree of protection of the mounting space | IP54
Degree of protection of clips or terminals | IP20
Ambient temperature | -25 ... +45 °C
Storage and transport temperature | -40 ... +85 °C
Resistance to vibrations | 10 ... 55 Hz, Amplitude 0.35 mm
Restistance to shock | 10 g / 11 ms
Ambient conditions - Insulation values
Rated impulse withstand voltage Uimp | 4 kV
Overvoltage category | III
Degree of pollution | 2
Electrical data
Operating voltage | 24 VDC -10 % / +20 %
Ripple voltage | 10 %
Rated operating voltage | 24 VDC
Rated AC voltage for controls at DC minimum | 20.4 VDC
Rated control voltage at DC, maximum | 28.8 VDC
Electrical power consumption | 4.4 W
Contact resistance, maximum | 0.1 Ω
Note (Contact resistance) | in new state
Drop-out delay in case of power failure, typically | 80 ms
Drop-out delay in case of emergency, typically | 20 ms
Pull-in delay at automatic start, maximum, typically | 100 ms
ON delay at automatic start | Adjustable
Pull-in delay at RESET, typically | 20 ms
Material of the contacts, electrical | Ag-Ni, self-cleaning, positive drive
Electrical data - Safe relay outputs
Voltage, Utilisation category AC-15 | 250 VAC
Current, Utilisation category AC-15 | 6 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 6 A
Switching capacity, minimum | 10 VDC
Switching capacity, minimum | 10 mA
Switching capacity, maximum | 250 VAC
Switching capacity, maximum | 8 A
Electrical data - Digital inputs
Conduction resistance, maximum | 40 Ω
Electrical data - Relay outputs (auxiliary contacts)
Switching capacity, maximum | 24 VDC
Switching capacity, maximum | 2 A
Electrical data - Electromagnetic compatibility (EMC)
EMC rating | EMC-Directive
Status indication
Indicated operating states | Position relay K2 Position relay K1 Internal operating voltage Ui Position relay K3
Other data
Note (applications) | Safety sensor Guard system Pull-wire emergency stop switches Emergency stop button
Note
Note (General) | Inductive loads (e.g. contactors, relays, etc.) are to be suppressed by means of a suitable circuit.
Note (Cross-circuit detection) | Level 1
Wiring example
Note (Wiring diagram) | The wiring diagram is shown with guard doors closed and in de-energised condition. Relay outputs: Suitable for 2 channel control, for increase in capacity or number of contacts by means of contactors or relays with positive-guided contacts. The control recognises cross-short, cable break and earth leakages in the monitoring circuit. Input level: the example shows a 2-channel control of an Emergency Stop command device (level 1) with external reset button (R), and guard door monitoring (level 2) with feedback circuit (H2). Automatic start (level 1): The automatic start is programmed by connecting the feedback circuit to the terminals X1/+24 V DC. Automatic start (level 2): The automatic start is programmed by connecting the feedback circuit to the terminals X2/+24 V DC. If the feedback circuit is not required, establish a bridge. 1 NC contact each time communicates the status of level 1 and level 2
Schmersal India Pvt. Ltd., Plot No - G-7/1, Ranjangaon MIDC, Tal. - Shirur, Dist.- Pune 412 220
The details and data referred to have been carefully checked. Images may diverge from original. Further technical data can be found in the manual. Technical amendments and errors possible.
Generated on: 29/03/2024, 12:51 pm