## Worksheet
PSC1-C-100-FB10-MT
| Memory card conversion of the field bus protocols by software integrated SD-Bus-Gateway Modularly expandable to up to 272 safe inputs / outputs Safe spindle monitoring To EN 61800-5-2 (Safe Drive Monitoring) for up to 12 spindles | 4 safe 2 A pp-switching semiconductor outputs, switchable to 2 safe p- / n-switching semiconductor outputs 14 safe inputs on the base module 20 switchable, safe inputs / outputs 6 Signalling outputs 2 safety relay contacts
Ordering data
Product type description | PSC1-C-100-FB10-MT
Article number (order number) | 103049453
EAN (European Article Number) | 4030661623993
eCl@ss number, version 12.0 | 27-24-22-07
eCl@ss number, version 11.0 | 27-24-22-07
eCl@ss number, version 9.0 | 27-24-22-07
ETIM number, version 7.0 | EC000236
ETIM number, version 6.0 | EC000236
Approvals - Standards
Certificates | TÜV cULus
General data
Gross weight | 974 g
General data - Features
SD Card Slot | Yes
Master-Master-Kommunikation | No
Integrated SD gateway | Yes
Number of pulse outputs (test pulse output) | 6
Number of relay outputs (1-channel) | 2
Number of digital fail-safe inputs | 14
Number of digital fail-safe in-/outputs | 20
Number of fail-safe digital outputs | 4
Number of signalling outputs | 6
Anzahl der Erweiterungsbaugruppen, maximal | 8
<table><tr><td>Safety classification</td></tr></table>
Performance Level, up to | e
Category | 4
PFH value | 1.22 x 10⁻⁸ /h
Safety Integrity Level (SIL), suitable for applications in | 3
Mission time | 20 Year(s)
Mechanical data
Mounting | can be clipped into standard rail
Mechanical data - Connection technique
Cable section, minimum | 0.2 mm²
Cable section, maximum | 2.5 mm²
Wire cross-section, minimum | 24 AWG
Wire cross-section, maximum | 12 AWG
Wire cross-section | 24 ... 12 AWG
Terminal (mechanical) | Removable screw terminals
Mechanical data - Dimensions
Width | 112.5 mm
Height | 100 mm
Depth | 115 mm
Ambient conditions
Degree of protection | IP20
Ambient temperature | +0 ... +50 °C
Storage and transport temperature | -25 ... +70 °C
Relative humidity, minimum | 5 %
Relative humidity, maximum | 85 %
Note (Relative humidity) | non-condensing
Permissible installation altitude above sea level, maximum | 2,000 m
Ambient conditions - Insulation values
Overvoltage category | III
Degree of pollution | 2
Electrical data
Operating voltage | 24 VDC -15 % / +20 %
Rated operating voltage | 24 VDC
Electrical data - Universal communication interface
Designation, Communication interface | RJ45
Electrical data - Communication protocols
Feldbus Protokoll | Modbus TCP
Electrical data - Safety digital outputs
Rated operating current (safety outputs) | 2,000 mA
Design of control elements | short-circuit proof, p-type (Q2 und Q3)
Electrical data - Safe relay outputs
Voltage, Utilisation category AC-15 | 230 VAC
Current, Utilisation category AC-15 | 2 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 2 A
Electrical data - Electromagnetic compatibility (EMC)
Electromagnetic compatibility | DIN EN 62061 DIN EN 61800-3
Interfering radiation | DIN EN 61000-6-4
EMC rating | DIN EN 61000-6-7 DIN EN 61326-3 DIN EN 61000-6-2
Scope of delivery
Scope of delivery | Backplane bus connector Connector terminals
K.A. Schmersal GmbH & Co. KG, Möddinghofe 30, 42279 Wuppertal
The details and data referred to have been carefully checked. Images may diverge from original. Further technical data can be found in the manual. Technical amendments and errors possible.
Generated on: 29/03/2025, 03:15