## Worksheet
CSS 14-34-S-SD-M-L
| 1 x Pre-wired cable 8-pole Actuation from side serial diagnostic output Max. 31 sensors can be wired in series. Thermoplastic enclosure Electronic contact-free, coded system | Misaligned actuation possible 27 mm x 108.2 mm x 35 mm High repeat accuracy of the switching points Max. length of the sensor chain 200 m 2 short-circuit proof PNP safety outputs Integral cross-short, wire-breakage and external voltage monitoring of the safety cables up to the control cabinet
Ordering data
Product type description | CSS 14-34-S-SD-M-L
Article number (order number) | 101181061
EAN (European Article Number) | 4030661314853
eCl@ss number, version 12.0 | 27-27-46-01
eCl@ss number, version 11.0 | 27-27-24-03
eCl@ss number, version 9.0 | 27-27-24-03
ETIM number, version 7.0 | EC001829
ETIM number, version 6.0 | EC001829
Approvals - Standards
Certificates | cULus
General data
Standards | EN IEC 60947-5-3
Working principle | inductive
Housing construction form | Block
Installation conditions (mechanical) | not flush
Sensor topology | Sensor for series wiring
Housing material | Glass-fibre, reinforced thermoplastic
Active area | Glass-fibre, reinforced thermoplastic
Reaction time, maximum | 30 ms
Duration of risk, maximum | 60 ms
Gross weight | 295 g
General data - Features
Serial diagnostics | Yes
Diagnostic output | Yes
Short circuit detection | Yes
Cross-circuit detection | Yes
Safety functions | Yes
Cascadable | Yes
Integral system diagnostics, status | Yes
Number of LEDs | 3
Number of semi-conductor outputs with signaling function | 1
Number of fail-safe digital outputs | 2
Number of series-wiring of sensors | 31
<table><tr><td>Safety classification</td></tr></table>
Vorschriften | EN ISO 13849-1 EN IEC 60947-5-3 EN IEC 61508
Performance Level, up to | e
Category | 4
PFH value | 3.60 x 10⁻⁹ /h
Safety Integrity Level (SIL), suitable for applications in | 3
Mission time | 20 Year(s)
Mechanical data
Actuating panels | lateral
Active area | lateral
Switching distance actuator | Actuator CST 34-V-1: 10 mm (typical switch distance Sn) Betätiger CST 34-V-1: 8 mm (gesicherter Schaltabstand EIN Sao) Betätiger CST 34-V-1: 13 mm (gesicherter Schaltabstand AUS Sar) Actuator CST 34-S-1 / CST 34-S-3: 14 mm (typical switch distance Sn) Actuator CST 34-S-1 / CST 34-S-3: 12 mm (ensured switch distance ON Sao) Actuator CST 34-S-1 / CST 34-S-3:: 17 mm (ensured switch distance OFF Sar) Actuator CST 34-S-2: 14 mm (typical switch distance Sn) Actuator CST 34-S-2: 12 mm (ensured switch distance ON Sao) Betätiger CST 34-S-2: 17 mm (gesicherter Schaltabstand AUS Sar) Betätiger CST 180-1 / CST 180-2: 10 mm (typischer Schaltabstand Sn) Actuator CST 180-1 / CST 180-2: 8 mm (ensured switch distance ON Sao) Actuator CST 180-1 / CST 180-2: 13 mm (ensured switch distance OFF Sar)
Mechanical data - Switching distances
Hysteresis (Switching distance), maximum | 1.5 mm
Repeat accuracy R | 0.5 mm
Note (Repeat accuracy R) | Axial offset: The long side allows for a maximum height misalignment (x) of sensor and actuator of 36 mm (e.g. mounting tolerance or due to guard door sagging). Increased misalignment, max. 53 mm, possible when the CST 34-S-2 actuator is used. The axial misalignment (y) is max. ± 10 mm (see figure: Operating principle)
Mechanical data - Connection technique
Note (length of the sensor chain) | Cable length and cross-section change the voltage drop dependiing on the output current
Note (series-wiring) | Unlimited number of devices, oberserve external line fusing, max. 31 devices in case of serial diagnostic SD
Length of cable | 1 m
Termination | Cable (Y-UL 2517), 8-pole
Cable section, maximum | 8 x 0.35 mm²
Wire cross-section | 22 AWG
Cable type | LiYY
Mechanical data - Dimensions
Length of sensor | 35 mm
Width of sensor | 27 mm
Height of sensor | 108.2 mm
Ambient conditions
Degree of protection | IP65 IP67
Ambient temperature | -25 ... +70 °C
Storage and transport temperature | -25 ... +85 °C
Resistance to vibrations | 10 … 55 Hz, amplitude 1 mm
Restistance to shock | 30 g / 11 ms
Protection class | II
Ambient conditions - Insulation values
Rated insulation voltage Ui | 32 VDC
Rated impulse withstand voltage Uimp | 0.8 kV
Overvoltage category | III
Degree of pollution | 3
Electrical data
No-load supply current I0, typical | 100 mA
Operating current | 600 mA
Required rated short-circuit current | 100 A
Switching frequency, approx. | 3 Hz
Electrical data - Safety digital outputs
Rated operating current (safety outputs) | 250 mA
Output current, (fail-safe output), maximum | 0.25 A
Design of control elements | p-type
Voltage drop Ud, maximum | 0.5 V
Leakage current Ir, maximum | 0.5 mA
Voltage, Utilisation category DC-12 | 24 VDC
Current, Utilisation category DC-12 | 0.25 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 0.25 A
Electrical data - Diagnostic outputs
Design of control elements | p-type
Voltage drop Ud, maximum | 5 V
Electrical data - Serial diagnostic SD
Designation, Serial diagnostic SD | OUT
Operation current | 150 mA
Design of control elements | short-circuit proof, p-type
Wiring capacitance | 50 nF
Electrical data - Electromagnetic compatibility (EMC)
Interfering radiation | IEC 61000-6-4
EMC rating | IEC 61000-6-2
Pin assignment
PIN 1 | A1 Ue Brown
PIN 2 | X1 Safety input 1 White
PIN 3 | A2 GND Blue
PIN 4 | Y1 Safety output 1 Black
PIN 5 | SD serial diagnostic output: Grey
PIN 6 | X2 Safety input 2 violet
PIN 7 | Y2 Safety output 2 red
PIN 8 | IN serial diagnostic input Pink
Scope of delivery
Scope of delivery | Actuator must be ordered separately.
Accessory
Recommendation (actuator) | CST 34-S-2 CST 34-S-3 CST 180-1 CST 180-2 CST 34-S-1
Recommended safety switchgear | PROTECT PSC1 SRB-E-301ST SRB-E-201LC
Note
Note (General) | Evaluation requirements: dual-channel safety input, suitable for p-type sensors with NO function. The safety-monitoring module must tolerate internal functional tests of the sensors with cyclic switch-off of the sensor outputs for max. 0.5 ms. Short-circuit recognition by the evaluation is not necessary.
K.A. Schmersal GmbH & Co. KG, Möddinghofe 30, 42279 Wuppertal
The details and data referred to have been carefully checked. Images may diverge from original. Further technical data can be found in the manual. Technical amendments and errors possible.
Generated on: 01/06/2025, 19:25