## Worksheet
SRB220XV2 / V.2
2 safety contacts, STOP 0; 2 safety contacts, STOP 1 Suitable for the signal processing of outputs with contact sensors Suitable for signal processing of outputs connected to potentials (AOPDs), e.g. safety light grids/curtains
Ordering data
Replacement article number | 101188429
Product type description | SRB220XV2 / V.2
Article number (order number) | 101195578
EAN (European Article Number) | 4250116202188
eCl@ss number, version 12.0 | 27-37-18-19
eCl@ss number, version 11.0 | 27-37-18-19
eCl@ss number, version 9.0 | 27-37-18-19
ETIM number, version 7.0 | EC001449
ETIM number, version 6.0 | EC001449
Available until | 31.12.2024
Approvals - Standards
Certificates | cULus
General data
Standards | EN IEC 62061 EN ISO 13849-1 EN IEC 60947-5-1 EN IEC 60947-5-3 EN IEC 60947-5-5 EN IEC 61508 EN IEC 60204-1 EN IEC 60947-1
Climatic stress | EN 60068-2-78
Housing material | Glass-fibre reinforced thermoplastic, ventilated
Gross weight | 420 g
General data - Features
Electronic Fuse | Yes
Wire breakage detection | Yes
Cross-circuit detection | Yes
Start input | Yes
Feedback circuit | Yes
Automatic reset function | Yes
Reset edge detection | Yes
Earth connection detection | Yes
Integral system diagnostics, status | Yes
Number of LEDs | 5
Number of normally closed (NC) | 2
Number of safety contacts | 4
Number of Safety contacts, STOP 0 | 3
Number of Safety contacts, STOP 1 | 2
<table><tr><td>Safety classification</td></tr></table>
Standards | EN IEC 60947-5-1 EN IEC 61508
Stop-Category | 0 1
<table><tr><td>Safety classification - Relay outputs</td></tr></table>
Performance Level, stop 0, up to | e
Performance Level, stop 1, up to | d
Category, Stop 0 | 4
Category, Stop 1 | 3
Diagnostic Coverage (DC) Level, Stop 0 | ≥ 99 %
Diagnostic Coverage (DC) Level, Stop 1 | &gt; 60
PFH value, Stop 0 | 2.00 x 10⁻⁸ /h
PFH value, Stop 1 | 2.00 x 10⁻⁷ /h
Safety Integrity Level (SIL), Stop 0, suitable for applications in | 3
Safety Integrity Level (SIL), Stop 1, suitable for applications in | 2
Mission time | 20 Year(s)
Common Cause Failure (CCF), minimum | 65
PFD value | 5.30 x 10⁻⁵
PFD value | 5.30 x 10⁻⁵
Mechanical data
Mechanical life, minimum | 10,000,000 Operations
Mounting | Snaps onto standard DIN rail to EN 60715
Mechanical data - Connection technique
Terminal designations | IEC/EN 60947-1
Termination | rigid or flexible Screw terminals M20 x 1.5
Cable section, minimum | 0.25 mm²
Cable section, maximum | 2.5 mm²
Tightening torque of Clips | 0.6 Nm
Mechanical data - Dimensions
Width | 45 mm
Height | 100 mm
Depth | 121 mm
Ambient conditions
Degree of protection of the enclosure | IP40
Degree of protection of the mounting space | IP54
Degree of protection of clips or terminals | IP20
Ambient temperature | -25 ... +60 °C
Storage and transport temperature | -40 ... +85 °C
Resistance to vibrations | 10...55 Hz, Amplitude 0.35 mm, ± 15 %
Restistance to shock | 30 g / 11 ms
Ambient conditions - Insulation values
Rated impulse withstand voltage Uimp | 4 kV
Overvoltage category | III
Degree of pollution | 2
Electrical data
Frequency range | 50 Hz 60 Hz
Operating voltage | 24 VAC -15 % / +10 %24 VDC -15 % / +20 %
Ripple voltage | 10 %
Rated operating voltage | 24 VAC
Rated operating voltage | 24 VDC
Rated AC voltage for controls, 50 Hz, minimum | 20.4 VAC
Rated control voltage at AC 50 Hz, maximum | 26.4 VAC
Rated AC voltage for controls, 60 Hz, minimum | 20.4 VAC
Rated control voltage at AC 60 Hz, maximum | 26.4 VAC
Rated AC voltage for controls at DC minimum | 20.4 VDC
Rated control voltage at DC, maximum | 28.8 VDC
Electrical power consumption | 2.6 W
Electrical power consumption | 5.4 VA
Contact resistance, maximum | 0.1 Ω
Note (Contact resistance) | in new state
Drop-out delay in case of power failure, typically | 80 ms
Drop-out delay in case of emergency, typically | 30 ms
Pull-in delay at automatic start, maximum, typically | 250 ms
Pull-in delay at RESET, typically | 20 ms
Material of the contacts, electrical | AgSn0, Ag-Ni, self-cleaning, positive drive
Electrical data - Safe relay outputs
Voltage, Utilisation category AC-15 | 230 VAC
Current, Utilisation category AC-15 | 6 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 6 A
Switching capacity, minimum | 10 VDC
Switching capacity, minimum | 10 mA
Switching capacity, maximum | 250 VAC
Switching capacity, maximum | 8 A
Electrical data - Safe relay outputs
Voltage, Utilisation category AC-15 | 230 VAC
Current, Utilisation category AC-15 | 3 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 2 A
Switching capacity, minimum | 10 VDC
Switching capacity, minimum | 10 mA
Switching capacity, maximum | 250 VAC
Switching capacity, maximum | 6 A
Electrical data - Digital inputs
Conduction resistance, maximum | 40 Ω
Electrical data - Digital Output
Voltage, Utilisation category DC-12 | 24 VDC
Current, Utilisation category DC-12 | 0.1 A
Electrical data - Relay outputs (auxiliary contacts)
Switching capacity, maximum | 24 VDC
Switching capacity, maximum | 2 A
Electrical data - Electromagnetic compatibility (EMC)
EMC rating | EMC-Directive
Status indication
Indicated operating states | Position relay K2 Position relay K1 Internal operating voltage Ui Position relay K3
Other data
Note (applications) | Guard system Emergency-Stop button Pull-wire emergency stop switches Safety light curtain
Note
Note (General) | Inductive loads (e.g. contactors, relays, etc.) are to be suppressed by means of a suitable circuit.
Wiring example
Note (Wiring diagram) | The wiring diagram is shown with guard doors closed and in de-energised condition. The control recognises cross-short, cable break and earth leakages in the monitoring circuit. 2 channel control shown for a guard-door monitor with two contacts, of which at least one contact has positive break, with external reset button (R). (H2) = Feedback circuit
K.A. Schmersal GmbH & Co. KG, Möddinghofe 30, 42279 Wuppertal
The details and data referred to have been carefully checked. Images may diverge from original. Further technical data can be found in the manual. Technical amendments and errors possible.
Generated on: 15/08/2024, 09:30