## Worksheet
SRB200EXi-1A
Automatic reset function 2 safety contacts Suitable for signal processing of emergency stop control devices, interlocking equipment, etc
Ordering data
Product type description | SRB200EXi-1A
Article number (order number) | 103037577
EAN (European Article Number) | 4030661544939
eCl@ss number, version 12.0 | 27-37-18-19
eCl@ss number, version 11.0 | 27-37-18-19
eCl@ss number, version 9.0 | 27-37-18-19
ETIM number, version 7.0 | EC001449
ETIM number, version 6.0 | EC001449
Explosion protection
Explosion protection: regulations | EN IEC 60079-0 EN 60079-11 EN IEC 60079-15
Explosion protection zones | 2
Explosion protection category | 3G
Explosion protection designation | EX II 3 G Ex nA nC IIC T5 Gc (Installation SRB, in Zone 2) EX II (2) G [Ex ib Gb] IIC EX II (2) D [Ex ib Db] IIIC
General data
Climatic stress | EN 60068-2-78
Housing material | Glass-fibre reinforced thermoplastic, ventilated
Gross weight | 266 g
General data - Features
Wire breakage detection | Yes
Cross-circuit detection | Yes
Earth connection detection | Yes
Integral system diagnostics, status | Yes
Number of LEDs | 5
Number of normally closed (NC) | 2
Number of safety contacts | 2
<table><tr><td>Safety classification</td></tr></table>
Standards | EN ISO 13849-1 EN IEC 60947-5-1 EN IEC 61508
Stop-Category | 0
<table><tr><td>Safety classification - Relay outputs</td></tr></table>
Performance Level, stop 0, up to | e
Category, Stop 0 | 4
Diagnostic Coverage (DC) Level, Stop 0 | ≥ 99 %
PFH value, Stop 0 | 2.00 x 10⁻⁸ /h
Safety Integrity Level (SIL), Stop 0, suitable for applications in | 3
Mission time | 15 Year(s)
Common Cause Failure (CCF), minimum | 65
Mechanical data
Mechanical life, minimum | 10,000,000 Operations
Mounting | Snaps onto standard DIN rail to EN 60715
Mechanical data - Connection technique
Terminal designations | IEC/EN 60947-1
Mechanical data - Dimensions
Width | 22.5 mm
Height | 100 mm
Depth | 121 mm
Ambient conditions
Degree of protection of the enclosure | IP40
Degree of protection of the mounting space | IP54
Degree of protection of clips or terminals | IP20
Ambient temperature | -25 ... +60 °C
Storage and transport temperature | -40 ... +85 °C
Resistance to vibrations | 10 ... 55 Hz, Amplitude 0.35 mm
Restistance to shock | 30 g / 11 ms
Ambient conditions - Insulation values
Rated impulse withstand voltage Uimp | 4 kV
Overvoltage category | III
Degree of pollution | 2
Electrical data
Operating voltage | 24 VDC -10 % / +20 %
Ripple voltage | 10 %
Current consumption | 57 mA
Rated operating voltage | 24 VDC
Rated AC voltage for controls at DC minimum | 20.4 VDC
Rated control voltage at DC, maximum | 28.8 VDC
Utilisation category AC-15 | 230 VAC
Utilisation category AC-15 | 2 A
Utilisation category DC-13 | 24 VDC
Utilisation category DC-13 | 2 A
Contact resistance, maximum | 0.1 Ω
Note (Contact resistance) | in new state
Drop-out delay in case of power failure, typically | 20 ms
Drop-out delay in case of &quot;emergency stop&quot;, maximum | 20 ms
Pull-in delay at automatic start, maximum, typically | 300 ms
Pull-in delay at RESET, typically | 20 ms
Material of the contacts, electrical | AgSn0. self-cleaning, positive drive
Electrical data - Digital inputs
Conduction resistance, maximum | 30 Ω
Electrical data - Electromagnetic compatibility (EMC)
EMC rating | EMC-Directive
Other data
Note (applications) | Safety sensor Guard system Emergency-Stop button Pull-wire emergency stop switches
Note
Note (General) | Inductive loads (e.g. contactors, relays, etc.) are to be suppressed by means of a suitable circuit.
Wiring example
Note (Wiring diagram) | The wiring diagram is shown with guard doors closed and in de-energised condition. Monitoring 1 guard door(s), each with a magnetic safety sensor of the BNS range If only one external relay or contactor is used to switch the load, the system can be classified in Control Category 3 to ISO 13849-1, if exclusion of the fault “Failure of the external contactor” can be substantiated and is documented, e.g. by using a reliable down-rated contactor. A second contactor leads to an increase in the level of security by redundant switching to switch the load off. To secure a guard door up to PL e and Category 4 The feedback circuit monitors the position of the contactors KA and KB. Automatic start: The automatic start is programmed by connecting the feedback circuit to the terminals X1/X2. If the feedback circuit is not required, establish a bridge.
Schmersal, Inc., 115 E Stevens Ave, Suite 208, Valhalla, NY 10595
The details and data referred to have been carefully checked. Images may diverge from original. Further technical data can be found in the manual. Technical amendments and errors possible.
Generated on: 5/4/2024, 6:13 PM