## Worksheet
TS 452-21Y
Metal enclosure 118 mm x 127 mm x 64 mm ( basic component) 2 cable entries M 20 x 1.5
Ordering data
Note (Delivery capacity) | Not available!
Product type description | TS 452-21Y
Article number (order number) | 101058413
eCl@ss number, version 12.0 | 27-27-06-01
eCl@ss number, version 11.0 | 27-27-06-01
eCl@ss number, version 9.0 | 27-27-06-01
ETIM number, version 7.0 | EC000030
ETIM number, version 6.0 | EC000030
Approvals - Standards
Certificates | CCC
General data
Standards | EN IEC 60947-5-1
Working principle | mechanical
Slide form | Sphere
Housing material | Grey cast iron, galvanised
Housing coating material | painted
Gross weight | 1,800 g
General data - Features
Number of normally closed (NC) | 1
Number of normally open (NO) | 2
Mechanical data
Actuating element | Plunger
Mechanical life, minimum | 10,000,000 Operations
Actuating angle | 20 °
Contact opening | 2 x 6 mm
Actuating speed, minimum | 1 mm/min
Actuating speed, maximum | 1 m/s
Note (Actuating speed) | Actuating speed with vertical actuating angle to switch axis
Mechanical data - Connection technique
Termination | Screw terminals M20 x 1.5
Cable section, minimum | 1.5 mm²
Cable section, maximum | 2.5 mm²
Note | All indications including the conductor ferrules.
Wire cross-section | 13 AWG
Mechanical data - Dimensions
Length of sensor | 64 mm
Width of sensor | 118 mm
Height of sensor | 153 mm
Diameter of the Plunger | 10 mm
Ambient conditions
Degree of protection | IP65
Ambient temperature | -30 ... +90 °C
Ambient conditions - Insulation values
Rated insulation voltage Ui | 400 V
Rated impulse withstand voltage Uimp | 6 kV
Electrical data
Thermal test current | 16 A
Utilisation category AC-15 | 400 VAC
Utilisation category AC-15 | 4 A
Switching element | NO contact, NC contact
Note (Switching element) | with double break
Switching principle | Slow action
Material of the contacts, electrical | Silver
Note
Note (General) | Actuation from the side of the plunger should be avoided, since this reduces the mechanical life of the position switch.
Schmersal, Inc., 115 E Stevens Ave, Suite 208, Valhalla, NY 10595
The details and data referred to have been carefully checked. Images may diverge from original. Further technical data can be found in the manual. Technical amendments and errors possible.
Generated on: 7/1/2025, 1:16 PM