## Worksheet
AZR31S1-2SEC./230VAC
| Fail-safe standstill monitors Sensor-free detection of standstill by monitoring e.m.f. Direct connection to three-phase motors Suitable for connection to a frequency converter with the following interface date: rotary hysteresis 0 ... 1000 Hz; switching frequency of the end level up to 16 kHz; engine voltage range 0 ... 400 V | This fail-safe standstill monitor has the particular advantage that no adjustment for a required-value is needed during comissioning. 3 safety contacts, STOP 0 1 Signalling output
Ordering data
Note (Delivery capacity) | Not available!
Product type description | AZR31S1-2SEC./230VAC
Article number (order number) | 101179105
EAN (European Article Number) | 4030661446554
eCl@ss number, version 12.0 | 27-37-18-19
eCl@ss number, version 11.0 | 27-37-18-19
eCl@ss number, version 9.0 | 27-37-18-19
ETIM number, version 7.0 | EC001449
ETIM number, version 6.0 | EC001449
General data
Standards | EN IEC 62061 EN ISO 13849-1 EN IEC 60947-5-1 EN IEC 60947-5-3 EN IEC 60947-5-5 EN IEC 61508 EN IEC 60204-1 EN IEC 60947-1
Climatic stress | EN 60068-2-78
Housing material | Glass-fibre, reinforced thermoplastic
Gross weight | 400 g
General data - Features
Wire breakage detection | Yes
Cross-circuit detection | Yes
Feedback circuit | Yes
Automatic reset function | Yes
Earth connection detection | Yes
Integral system diagnostics, status | Yes
Number of auxiliary contacts | 1
Number of LEDs | 5
Number of safety contacts | 3
<table><tr><td>Safety classification</td></tr></table>
Standards | EN IEC 60947-5-1 EN IEC 61508
PFH value | 2.00 x 10⁻⁸ /h
Mission time | 20 Year(s)
Common Cause Failure (CCF), minimum | 65
Stop-Category | 0
<table><tr><td>Safety classification - Relay outputs</td></tr></table>
Performance Level, stop 0, up to | e
Category, Stop 0 | 4
Diagnostic Coverage (DC) Level, Stop 0 | ≥ 99 %
Safety Integrity Level (SIL), Stop 0, suitable for applications in | 3
Mechanical data
Mechanical life, minimum | 10,000,000 Operations
Mounting | Snaps onto standard DIN rail to EN 60715
Mechanical data - Connection technique
Terminal designations | IEC/EN 60947-1
Termination | rigid or flexible Screw terminals M20 x 1.5
Cable section, minimum | 0.25 mm²
Cable section, maximum | 2.5 mm²
Tightening torque of Clips | 0.6 Nm
Mechanical data - Dimensions
Width | 45 mm
Height | 73.2 mm
Depth | 121 mm
Ambient conditions
Degree of protection of the enclosure | IP40
Degree of protection of the mounting space | IP54
Degree of protection of clips or terminals | IP20
Ambient temperature | -25 ... +45 °C
Storage and transport temperature | -40 ... +85 °C
Resistance to vibrations | 10 ... 55 Hz, Amplitude 0.35 mm
Restistance to shock | 30 g / 11 ms
Ambient conditions - Insulation values
Rated impulse withstand voltage Uimp | 4 kV
Overvoltage category | III
Degree of pollution | 2
Electrical data
Frequency range | 50 Hz 60 Hz
Operating voltage | 230 VAC -15 % / +10 %
Rated operating voltage | 230 VAC
Rated AC voltage for controls, 50 Hz, minimum | 195.5 VAC
Rated control voltage at AC 50 Hz, maximum | 253 VAC
Rated AC voltage for controls, 60 Hz, minimum | 195.5 VAC
Rated control voltage at AC 60 Hz, maximum | 253 VAC
Electrical power consumption, maximum | 4 VA
Contact resistance, maximum | 0.1 Ω
Note (Contact resistance) | in new state
Cable length (Master/Slave), maximum | 10 m
Drop-out delay in case of power failure, typically | 80 ms
Drop-out delay in case of emergency, typically | 20 ms
Drop-out delay in case of &quot;emergency stop&quot;, maximum | 15 ms
Pull-in delay at automatic start (after detecting standstill), approx. | 2,000 ms
Pull-in delay at RESET, typically | 20 ms
Material of the contacts, electrical | AgSn0. self-cleaning, positive drive
Electrical data - Safe relay outputs
Voltage, Utilisation category AC-15 | 230 VAC
Current, Utilisation category AC-15 | 6 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 6 A
Switching capacity, minimum | 10 VDC
Switching capacity, minimum | 10 mA
Switching capacity, maximum | 250 VAC
Switching capacity, maximum | 8 A
Electrical data - Digital inputs
Conduction resistance, maximum | 40 Ω
Electrical data - Digital Output
Voltage, Utilisation category DC-12 | 24 VDC
Current, Utilisation category DC-12 | 0.1 A
Electrical data - Relay outputs (auxiliary contacts)
Switching capacity, maximum | 24 VDC
Switching capacity, maximum | 2 A
Electrical data - Electromagnetic compatibility (EMC)
EMC rating | EMC-Directive
Status indication
Indicated operating states | OUT, green: release ON, green: supply voltage UB ERR, red: error channel A + B
Other data
Note (applications) | safe standstill monitoring
Note
Note (General) | Inductive loads (e.g. contactors, relays, etc.) are to be suppressed by means of a suitable circuit.
Wiring example
Note (Wiring diagram) | The wiring diagram is shown with guard doors closed and in de-energised condition. The sensor-free standstill monitor checks the e.m.f. of the three phase motor. The SRB range guard door monitor checks the position of the guard door. Monitoring the guard door using a solenoid interlock and a safety switch with separate actuator (A and B). Release takes place by means of the NO contact (E) only when the run-down movement has been terminated. After release has taken place, the guard door must be opened. To secure a guard door
Schmersal, Inc., 115 E Stevens Ave, Suite 208, Valhalla, NY 10595
The details and data referred to have been carefully checked. Images may diverge from original. Further technical data can be found in the manual. Technical amendments and errors possible.
Generated on: 5/1/2024, 1:27 PM