## Worksheet
SFB-PN-IRT-8M12-IOP-V2
Safety fieldbox for PROFINET/PROFIsafe For connection of up to 8 safety switching devices Integrated dual-port switch, IRT-capable Protection class IP67
Ordering data
Product type description | SFB-PN-IRT-8M12-IOP-V2
Article number (order number) | 103040357
EAN (European Article Number) | 4030661561554
eCl@ss number, version 12.0 | 27-24-26-04
eCl@ss number, version 11.0 | 27-24-26-04
eCl@ss number, version 9.0 | 27-24-26-04
ETIM number, version 7.0 | EC001599
ETIM number, version 6.0 | EC001599
Approvals - Standards
Certificates | TÜV cULus PNO UKCA
General data
Standards | EN IEC 61131-1 EN IEC 61131-2 EN ISO 13849-1 EN IEC 60947-5-3 EN IEC 61508
Housing material | Thermoplastic, Polyamide PA 6 GF
Material of the identification label | Plastic, Polyamide PA
Material of viewing window | Polyamide PACM 12
Material of electronic encapsulation | Polyurethane 2K PU
Gross weight | 655 g
General data - Features
Integral system diagnostics, general | Yes
<table><tr><td>Safety classification</td></tr></table>
Standards | EN ISO 13849-1 EN IEC 61508
<table><tr><td>Safety classification - Safety inputs 2-channels</td></tr></table>
Performance Level, up to | e
Category | 4
Diagnostic Coverage (DC) Level | 99 %
PFH value | 1.10 x 10⁻⁹ /h
PFDavg | 9.60 x 10⁻⁵
Safety Integrity Level (SIL), suitable for applications in | 3
Mission time | 20 Year(s)
Response time of local safety input ⇒ Fieldbus, maximum | 20 ms
Notice | The SFB fulfils the requirements as PDDB (proximity switch with defined behaviour under fault conditions) according to EN 60947-5-3 in combination with magnetic sensors (2 NC contacts) up to PL e / SIL 3.
<table><tr><td>Safety classification - Safety inputs 1-channel</td></tr></table>
Performance Level, up to | d
Category | 2
Diagnostic Coverage (DC) Level | 90 %
PFH value | 2.30 x 10⁻⁷ /h
PFDavg | 2.00 x 10⁻²
Safety Integrity Level (SIL), suitable for applications in | 1
Mission time | 20 Year(s)
Response time of local safety input &gt; Fieldbus, maximum | 20 ms
Test interval for error detection | 10 s
<table><tr><td>Safety classification - Safety outputs 1-channel</td></tr></table>
Performance Level, up to | d
Category | 3
Diagnostic Coverage (DC) Level | 90 %
PFH value | 1.00 x 10⁻⁷ /h
PFDavg | 8.80 x 10⁻³
Safety Integrity Level (SIL), suitable for applications in | 2
Mission time | 20 Year(s)
Reaction time Fieldbus &gt; local safety output | 50 ms
<table><tr><td>Safety classification - Safety outputs 2-channels</td></tr></table>
Performance Level, up to | e
Category | 4
Diagnostic Coverage (DC) Level | 99 %
PFH value | 1.20 x 10⁻⁹ /h
PFDavg | 1.10 x 10⁻⁴
Safety Integrity Level (SIL), suitable for applications in | 3
Notes (Safety Integrity Level) | This product must only be replaced in the application by an identical product of type SFB-PN-IRT-8M12-IOP-V2 with part no. 103040357. The older product version has a lower safety level.
Mission time | 20 Year(s)
Reaction time Fieldbus &gt; local safety output | 50 ms
Mechanical data
Mounting | Screws
Type of the fixing screws | 2x M6
Tightening torque of the fixing screws, maximum | 3 Nm
Type of the fixing screws, viewing window | 2x TX10 (Torx)
Tightening torque of the fastening screws for the viewing window, maximum | 0.6 Nm
Mechanical data - Connection technique
Termination | M12 Connector socket/connector
Terminal connector, Input/Output | X0 - X7: M12, 8-pole, A-coded
Terminal Connector, Power I/O | M12 POWER, 4-pole, T-coded
Terminal Connector, Field bus | M12, 4-pole, D-coded
Tightening torque of electrical connection, minimum | 0.8 Nm
Tightening torque of electrical connection, maximum | 1.5 Nm
Mechanical data - Dimensions
Length | 222.8 mm
Width | 63 mm
Height | 36.1 mm
Ambient conditions
Degree of protection | IP67 IP66
Ambient temperature | -25 ... +55 °C
Storage and transport temperature | -25 ... +70 °C
Relative humidity, minimum | 10 %
Relative humidity, maximum | 95 %
Note (Relative humidity) | non-condensing
Resistance to vibrations | 10 … 150 Hz, amplitude 0.35 mm / 5 g
Restistance to shock | 30 g / 11 ms
Protection class | III
Permissible installation altitude above sea level, maximum | 2,000 m
Ambient conditions - Insulation values
Rated insulation voltage Ui | 32 VDC
Rated impulse withstand voltage Uimp | 0.8 kV
Overvoltage category | III
Degree of pollution | 3
Electrical data
Operating voltage | 24 VDC -15 % / +10 % (stabilised PELV power supply)
Current consumption | 200 mA
Rated operating voltage | 24 VDC
Operating current | 10,000 mA
Note (Electrical data, Fuse rating) | External fuse protection required ≤ 10A slow blow when used to UL 61010.
Time to readiness, maximum | 8,000 ms
Device Watchdog Time | 10 ms
Device Acknowledgement Time, maximum | 25 ms
Reaction Time Safety Input, maximum | 20 ms
Reaction Time Safety Output, maximum | 50 ms
Electrical data - Communication protocols
Feldbus Protokoll | PROFINET / PROFIsafe
Fieldbus specification | V2.3, Conformance Class C
Specification safety fieldbus | V2.4
Fieldbus properties | Media Redundancy Protocol (MRP) Fast Start Up
Fieldbus network load class | 3
Transfer rate | 100 Mbit/s Full Duplex
Adressing | Discovery and Configuration Protocol (DCP)
Integrated switch | Dual Port, 100 Mbit/s, IRT capable
Fieldbus services | I&amp;M0 ... I&amp;M3, SNMP, LLDP
Service interface | WEB-Interface HTTP
Electrical data - Device Ports
Bezeichnung, Geräteanschlüsse | X0 ... X7
Cable length, device port | 30 m
Electrical data - Power supply external devices
Designation, Power supply | A1 and A2
Rated operating voltage | 24 VDC
Rated operating current | 800 mA
Internal electrical fuse | 1.5 A (Integrated automatic resettable fuse)
Electrical data - Safety digital inputs
Designation, Safety inputs | X1 and X2
Switching thresholds | −3 V … 5 V (Low) 13 V ... 30 V (High)
Current consumption at 24 V | 6 mA
Permissible residual drive current | 1 mA
Test pulse duration, minimum | 0.01 ms
Test pulse duration, maximum | 1 ms
Test pulse interval, minimum | 20 ms
Test pulse interval, maximum | 120,000 ms
Classification ZVEI CB24I, Sink | C1
Classification ZVEI CB24I, Source | C1 C2 C3
Electrical data - Safety digital outputs
Designation, Safety outputs | DO
Design of control elements | short-circuit proof, p-type
Voltage drop Ud, maximum | 2 V
Leakage current Ir, maximum | 0.5 mA
Voltage, Utilisation category DC-12 | 24 VDC
Current, Utilisation category DC-12 | 0.8 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 0.8 A
Note, Utilisation category DC-13 | Inductive load, maximum 400 mH
Switching frequency, maximum | 1 Hz
Test pulse duration, maximum | 1 ms
Test pulse interval, minimum | 15 ms
Test pulse interval, maximum | 500 ms
Classification ZVEI CB24I, Source | C1
Classification ZVEI CB24I, Sink | C1
Electrical data - Diagnostic inputs / FB-Interface
Designation, Diagnostic inputs / FB-Interface | DI
Switching thresholds | −3 V … 5 V (Low) 15 V … 30 V (High)
Current consumption at 24V | 12 mA
Input debounce filter | 10 ms
Data transfer rate FB-Interface | 19,2 kBaud
Electrical data - Test pulse output
Designation, Test pulse outputs | Y1 and Y2
Design of control elements | short-circuit proof, p-type
Voltage drop Ud, maximum | 1 V
Current leakage Ir, maximum | 0.5 mA
Voltage, Utilisation category DC-12 | 24 VDC
Y1 rated current at 24 V | 15 mA
Y2 rated current at 24 V | 10 mA
Y2 rated current at 0 V | 30 mA
Test pulse interval, typical | 500 ms
Test pulse duration, maximum | 1 ms
Classification ZVEI CB24I, Sink | C1
Classification ZVEI CB24I, Source | C1
LED status display - LED 01
LED status | Error LED device port
LED position | E: 0 ... 7
LED colour | green/red
LED status display - LED 02
LED status | Input LED device port
LED position | I: 0 ... 7
LED colour | Yellow
LED status display - LED 03
LED status | LED Link Ethernet port
LED position | L: P1 + P2
LED colour | Green
LED status display - LED 04
LED status | LED Activity Ethernet port
LED position | A: P1 + P2
LED colour | Yellow
LED status display - LED 05
LED status | System fault LED
LED position | &quot;SF&quot;: Module
LED colour | green/red
LED status display - LED 06
LED status | BUS fault LED
LED position | &quot;BF&quot;: Module
LED colour | Red
LED status display - LED 07
LED status | Fieldbox error LED
LED position | &quot;Err&quot;: Module
LED colour | green/red
LED status display - LED 08
LED status | Power-LED fieldbox
LED position | &quot;Pwr&quot;: Module
LED colour | Green
Other data
Note (applications) | Safe field box with decentralised I/Os
Schmersal, Inc., 115 E Stevens Ave, Suite 208, Valhalla, NY 10595
The details and data referred to have been carefully checked. Images may diverge from original. Further technical data can be found in the manual. Technical amendments and errors possible.
Generated on: 5/2/2024, 11:00 AM