## Worksheet
SRB-E-232ST-CC
Plug-in spring-cage terminal blocks with coding STOP 0 / 1 Function 1 oder 2-channel control 2 Safety outputs STOP 0 3 safety contacts STOP 1 Drop-out delay 0 … 30
Ordering data
Product type description | SRB-E-232ST-CC
Article number (order number) | 103016575
EAN (European Article Number) | 4030661510408
eCl@ss number, version 12.0 | 27-37-18-19
eCl@ss number, version 11.0 | 27-37-18-19
eCl@ss number, version 9.0 | 27-37-18-19
ETIM number, version 7.0 | EC001449
ETIM number, version 6.0 | EC001449
Approvals - Standards
Certificates | cULus
General data
Standards | EN IEC 62061 EN ISO 13849-1 EN IEC 60947-5-1 EN IEC 60947-5-3 EN IEC 60947-5-5 EN IEC 61508 EN IEC 60204-1 EN IEC 60947-1
Housing material | Glass-fibre reinforced thermoplastic, ventilated
Gross weight | 250 g
General data - Features
Wire breakage detection | Yes
Cross-circuit detection | Yes
Removable Terminals | Yes
Start input | Yes
Feedback circuit | Yes
Automatic reset function | Yes
Reset edge detection | Yes
Earth connection detection | Yes
Integral system diagnostics, status | Yes
Integral system diagnostics, error code | Yes
Number of auxiliary contacts | 1
Number of LEDs | 6
Number of normally closed (NC) | 2
Number of normally open (NO) | 1
Number of Safety contacts, STOP 1 | 3
Number of safety digital outputs, Stop 0 | 2
Number of signalling outputs | 1
<table><tr><td>Safety classification</td></tr></table>
Vorschriften | EN ISO 13849-1 EN IEC 62061 EN IEC 61508
Stop-Category | 0 1
<table><tr><td>Safety classification - Relay outputs</td></tr></table>
Performance Level, up to | e
Category | 4
Diagnostic Coverage (DC) Level | > 94 %
PFH value | 1.25 x 10⁻⁸ /h
PFD value | 5.30 x 10⁻⁵
Safety Integrity Level (SIL), suitable for applications in | 3
Mission time | 20 Year(s)
Common Cause Failure (CCF), minimum | 65
<table><tr><td>Safety classification - Fail-safe digital outputs</td></tr></table>
Performance Level, up to | e
Category | 4
PFH value | 2.66 x 10⁻⁹ /h
PFD value | 2.42 x 10⁻⁵
Safety Integrity Level (SIL), suitable for applications in | 3
Mission time | 20 Year(s)
Mechanical data
Mechanical life, minimum | 10,000,000 Operations
Mounting | Snaps onto standard DIN rail to EN 60715
Mechanical data - Connection technique
Terminal designations | IEC/EN 60947-1
Termination | Cage clamp, plug-in rigid or flexible
Cable section, minimum | 0.25 mm²
Cable section, maximum | 1.5 mm²
Mechanical data - Dimensions
Width | 22.5 mm
Height | 98 mm
Depth | 115 mm
Ambient conditions
Degree of protection of the enclosure | IP40
Degree of protection of the mounting space | IP54
Degree of protection of clips or terminals | IP20
Ambient temperature | -25 ... +60 °C
Storage and transport temperature | -40 ... +85 °C
Resistance to vibrations | 10 ... 55 Hz, Amplitude 0.35 mm
Restistance to shock | 30 g / 11 ms
Ambient conditions - Insulation values
Rated impulse withstand voltage Uimp, relay output | 4 kV
Rated impulse withstand voltage Uimp, semiconductor output | 0.8 kV
Overvoltage category | III
Degree of pollution | 2
Electrical data
Operating voltage | 24 VDC -20 % / +20 %
Ripple voltage | 10 %
Rated operating voltage | 24 VDC
Rated AC voltage for controls at DC minimum | 19.2 VDC
Rated control voltage at DC, maximum | 28.8 VDC
Electrical power consumption | 3 W
Contact resistance, maximum | 0.1 Ω
Note (Contact resistance) | in new state
Drop-out delay in case of power failure, typically | 10 ms
Drop-out delay in case of emergency, typically | 10 ms
Pull-in delay at automatic start, maximum, typically | 150 ms
Pull-in delay at RESET, typically | 150 ms
Switching frequency, maximum | 0.3 Hz
Material of the contacts, electrical | Ag-Ni, self-cleaning, positive drive
Electrical data - Safety digital outputs
Voltage drop Ud, maximum | 0.5 V
Leakage current Ir, maximum | 1 mA
Voltage, Utilisation category DC-12 | 24 VDC
Current, Utilisation category DC-12 | 2 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 2 A
Electrical data - Safe relay outputs
Voltage, Utilisation category AC-15 | 230 VAC
Current, Utilisation category AC-15 | 4 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 4 A
Switching capacity, minimum | 10 VDC
Switching capacity, minimum | 10 mA
Switching capacity, maximum | 250 VAC
Switching capacity, maximum | 6 A
Electrical data - Digital inputs
Conduction resistance, maximum | 40 Ω
Electrical data - Digital Output
Voltage, Utilisation category DC-12 | 24 VDC
Current, Utilisation category DC-12 | 0.1 A
Electrical data - Relay outputs (auxiliary contacts)
Switching capacity, maximum | 24 VDC
Switching capacity, maximum | 1 A
Electrical data - Electromagnetic compatibility (EMC)
EMC rating | EMC-Directive
Status indication
Indicated operating states | Internal operating voltage Ui Baustein-Status Fault codes
Other data
Note (applications) | Safety sensor Guard system hinged safety guard Emergency-Stop button Pull-wire emergency stop switches Safety light curtain Safety light barriers
Schmersal, Inc., 115 E Stevens Ave, Suite 208, Valhalla, NY 10595
The details and data referred to have been carefully checked. Images may diverge from original. Further technical data can be found in the manual. Technical amendments and errors possible.
Generated on: 4/17/2025, 2:00 PM