## Worksheet
SRB101EXi-1A
Automatic reset function 1 safety contact Suitable for signal processing of emergency stop control devices, interlocking equipment, etc Installation in Ex-Zone 2
Ordering data
Note (Delivery capacity) | Nicht mehr lieferbar!
Product type description | SRB101EXi-1A
Article number (order number) | 101196285
EAN (European Article Number) | 4250116202379
eCl@ss number, version 12.0 | 27-37-18-19
eCl@ss number, version 11.0 | 27-37-18-19
eCl@ss number, version 9.0 | 27-37-18-19
ETIM number, version 7.0 | EC001449
ETIM number, version 6.0 | EC001449
Approvals - Standards
Certificates | ATEX IECEx INMETRO PESO
Explosion protection
Explosion protection: regulations | EN IEC 60079-0 EN 60079-11 EN IEC 60079-15
Explosion protection zones | 2
Explosion protection category | 3G
Explosion protection designation | EX II 3 G Ex nA nC IIC T5 Gc (Installation SRB, in Zone 2) EX II (2) G [Ex ib Gb] IIC EX II (2) D [Ex ib Db] IIIC
General data
Climatic stress | EN 60068-2-78
Housing material | Kunststoff, glasfaserverstärkter Thermoplast, belüftet
Gross weight | 230 g
General data - Features
Wire breakage detection | Ja
Cross-circuit detection | Ja
Feedback circuit | Ja
Automatic reset function | Ja
Earth connection detection | Ja
Integral system diagnostics, status | Ja
Number of auxiliary contacts | 1
Number of LEDs | 5
Number of normally closed (NC) | 2
Number of safety contacts | 1
<table><tr><td>Safety classification</td></tr></table>
Vorschriften | EN ISO 13849-1 EN IEC 60947-5-1 EN IEC 61508
Stop-Category | 0
<table><tr><td>Safety classification - Relay outputs</td></tr></table>
Performance Level, stop 0, up to | e
Category, Stop 0 | 4
Diagnostic Coverage (DC) Level, Stop 0 | ≥ 99 %
PFH value, Stop 0 | 2,00 x 10⁻⁸ /h
Safety Integrity Level (SIL), Stop 0, suitable for applications in | 3
Mission time | 15 Year(s)
Common Cause Failure (CCF), minimum | 65
Mechanical data
Mechanical life, minimum | 10.000.000 Operations
Mounting | Schnellbefestigung für Normschiene nach DIN EN 60715
Mechanical data - Connection technique
Terminal designations | IEC/EN 60947-1
Termination | starr oder flexibel Schraubanschluss M20 x 1.5
Cable section, minimum | 0,25 mm²
Cable section, maximum | 2,5 mm²
Tightening torque of Clips | 0,6 Nm
Mechanical data - Dimensions
Width | 22,5 mm
Height | 100 mm
Depth | 121 mm
Ambient conditions
Degree of protection of the enclosure | IP40
Degree of protection of the mounting space | IP54
Degree of protection of clips or terminals | IP20
Ambient temperature | -25 ... +60 °C
Storage and transport temperature | -40 ... +85 °C
Resistance to vibrations | 10 ... 55 Hz, Amplitude 0,35 mm
Restistance to shock | 30 g / 11 ms
Ambient conditions - Insulation values
Rated impulse withstand voltage Uimp | 4 kV
Overvoltage category | III
Degree of pollution | 2
Electrical data
Operating voltage | 24 VDC -10 % / +20 %
Ripple voltage | 10 %
Current consumption | 57 mA
Rated operating voltage | 24 VDC
Rated AC voltage for controls at DC minimum | 20,4 VDC
Rated control voltage at DC, maximum | 28,8 VDC
Utilisation category AC-15 | 230 VAC
Utilisation category AC-15 | 2 A
Utilisation category DC-13 | 24 VDC
Utilisation category DC-13 | 2 A
Electrical power consumption | 3 W
Contact resistance, maximum | 0,1 Ω
Note (Contact resistance) | in Neuzustand
Drop-out delay in case of power failure, typically | 20 ms
Drop-out delay in case of &quot;emergency stop&quot;, maximum | 20 ms
Pull-in delay at automatic start, maximum, typically | 300 ms
Pull-in delay at RESET, typically | 20 ms
Material of the contacts, electrical | AgSnO, selbstreinigend, zwangsgeführt
Electrical data - Digital inputs
Conduction resistance, maximum | 30 Ω
Electrical data - Electromagnetic compatibility (EMC)
EMC rating | EMV-Richtlinie
Other data
Note (applications) | Sicherheits-Sensor Schutzeinrichtung NOT-HALT-Taster Seilzug-Notschalter
Note
Note (General) | Induktive Verbraucher (Schütze, Relais etc.) sind durch eine geeignete Beschaltung zu entstören.
Wiring example
Note (Wiring diagram) | Das Schaltungsbeispiel ist bei geschlossenen Schutzeinrichtungen und im spannungslosen Zustand dargestellt. Überwachung von 1 Schutzeinrichtung(en) mit je einem magnetischen Sicherheits-Sensor der Reihe BNS Wird nur ein externes Relais oder Schütz zum Schalten der Last verwendet, kann das System in die Kategorie 3 gem. ISO 13849-1 eingestuft werden, wenn der Fehlerausschluss „Versagen des externen Schützes“ begründet und dokumentiert werden kann, z.B. bei Verwendung eines zuverlässigen, überdimensionierten Schützes. Ein zweites Schütz führt zur Erhöhung der Sicherheit durch redundante Abschaltung der Last. Zur Absicherung einer Schutzeinrichtung bis zu PL e und Kategorie 4 Der Rückführkreis überwacht die Stellung der Schütze KA und KB. Automatischer Start: Die Programmierung auf automatischen Start erfolgt durch die Einbindung des Rückführkreises an die Klemmen X1/X2. Bei nicht benötigtem Rückführkreis ist dieser durch eine Brücke zu ersetzen.
Schmersal India Pvt. Ltd., Plot No - G-7/1, Ranjangaon MIDC, Tal. - Shirur, Dist.- Pune 412 220
Die genannten Daten und Angaben wurden sorgfältig geprüft. Abbildungen können vom Original abweichen. Weitere technische Daten finden Sie in der Betriebsanleitung. Technische Änderungen und Irrtümer vorbehalten.
Generiert am: 09.04.2025, 09:40