## Worksheet
SRB301ST-24V-(V.2)
Suitable for the signal processing of outputs with contact sensors Suitable for signal processing of outputs connected to potentials (AOPDs), e.g. safety light grids/curtains Suitable for the signal processing of outputs with contact sensors 3 safety contacts, STOP 0 1 Signalling output
Ordering data
Product type description | SRB301ST-24V-(V.2)
Article number (order number) | 103006151
EAN (European Article Number) | 4030661521589
eCl@ss number, version 12.0 | 27-37-18-19
eCl@ss number, version 11.0 | 27-37-18-19
eCl@ss number, version 9.0 | 27-37-18-19
ETIM number, version 7.0 | EC001449
ETIM number, version 6.0 | EC001449
Notice | 停售产品
Approvals - Standards
Certificates | TÜV cULus CCC TILVA
General data
Standards | EN IEC 62061 EN 81-20/-50 EN ISO 13849-1 EN IEC 60947-5-1 EN IEC 60947-5-3 EN IEC 60947-5-5 EN IEC 61508 EN IEC 60204-1 EN IEC 60947-1
Climatic stress | EN 60068-2-78
Housing material | 玻璃纤维加固热塑塑料，带通风
Gross weight | 283 g
General data - Features
Electronic Fuse | 是
Wire breakage detection | 是
Cross-circuit detection | 是
Removable Terminals | 是
Start input | 是
Feedback circuit | 是
Automatic reset function | 是
Reset edge detection | 是
Earth connection detection | 是
Integral system diagnostics, status | 是
Number of auxiliary contacts | 1
Number of LEDs | 5
Number of normally closed (NC) | 2
Number of safety contacts | 3
<table><tr><td>Safety classification</td></tr></table>
Vorschriften | EN ISO 13849-1 EN IEC 62061 EN IEC 61508
Stop-Category | 0
<table><tr><td>Safety classification - Relay outputs</td></tr></table>
Performance Level, stop 0, up to | e
Category, Stop 0 | 4
Diagnostic Coverage (DC) Level, Stop 0 | ≥ 99 %
PFH value, Stop 0 | 2.00 x 10⁻⁸ /h
Safety Integrity Level (SIL), Stop 0, suitable for applications in | 3
Mission time | 20 Year(s)
Common Cause Failure (CCF), minimum | 65
Mechanical data
Mechanical life, minimum | 10,000,000 Operations
Mounting | DIN导轨快速安装，依据EN 60715
Mechanical data - Connection technique
Terminal designations | IEC/EN 60947-1
Termination | 硬线或软线 螺栓连接，插入
Cable section, minimum | .25 mm²
Cable section, maximum | 2.5 mm²
Tightening torque of Clips | 0.6 Nm
Mechanical data - Dimensions
Width | 22.5 mm
Height | 120 mm
Depth | 121 mm
Ambient conditions
Degree of protection of the enclosure | IP40
Degree of protection of the mounting space | IP54
Degree of protection of clips or terminals | IP20
Ambient temperature | -25 ... +60 °C
Storage and transport temperature | -40 ... +85 °C
Resistance to vibrations | 10 ... 55 Hz, 振幅 .35 mm
Restistance to shock | 30 g / 11 ms
Ambient conditions - Insulation values
Rated impulse withstand voltage Uimp | 4 kV
Overvoltage category | III
Degree of pollution | 2
Electrical data
Frequency range | 50 Hz 60 Hz
Operating voltage | 24 VAC -15 % / +10 %24 VDC -10 % / +20 %
Ripple voltage | 10 %
Rated operating voltage | 24 VAC
Rated operating voltage | 24 VDC
Rated AC voltage for controls, 50 Hz, minimum | 20.4 VAC
Rated control voltage at AC 50 Hz, maximum | 26.4 VAC
Rated AC voltage for controls, 60 Hz, minimum | 20.4 VAC
Rated control voltage at AC 60 Hz, maximum | 26.4 VAC
Rated AC voltage for controls at DC minimum | 20.4 VDC
Rated control voltage at DC, maximum | 28.8 VDC
Electrical power consumption | 2 W
Electrical power consumption | 4.9 VA
Contact resistance, maximum | 0.1 Ω
Note (Contact resistance) | 处于全新的状态
Drop-out delay in case of power failure, typically | 80 ms
Drop-out delay in case of emergency, typically | 20 ms
Pull-in delay at automatic start, maximum, typically | 100 ms
Pull-in delay at RESET, typically | 20 ms
Material of the contacts, electrical | 氧化锡银，自清洁，强制定位
Electrical data - Safe relay outputs
Voltage, Utilisation category AC-15 | 230 VAC
Current, Utilisation category AC-15 | 6 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 6 A
Switching capacity, minimum | 10 VDC
Switching capacity, minimum | 10 mA
Switching capacity, maximum | 250 VAC
Switching capacity, maximum | 8 A
Electrical data - Digital inputs
Conduction resistance, maximum | 40 Ω
Electrical data - Relay outputs (auxiliary contacts)
Switching capacity, maximum | 24 VDC
Switching capacity, maximum | 2 A
Electrical data - Electromagnetic compatibility (EMC)
EMC rating | EMC指令
Status indication
Note (LED switching conditions display) | QS：交叉短路检测状态（当交叉短路检测处于激活状态时，LED亮起）。
Indicated operating states | 位置继电器 K2 位置继电器 K1 内部工作电压 Ui
Other data
Note (applications) | 安全传感器 防护系统 紧急停止按钮 紧急停止拉绳开关 安全光电开关
Note
Note (General) | 感应负载（例如接触器、继电器等）必须通过适当的电路抑制。
Wiring example
Note (Wiring diagram) | 接线图显示的是防护门关闭且处于断电状态的情况。 输入电平：该示例显示了带有两个限位开关的防护门监控的双通道控制，其中一个限位开关具有肯定断开、外部重置按钮（R）和反馈电路（H2）。 继电器输出：适用于双通道控制，用于增强触点容量或增加触点数量，通过使用接触器或带强制定位触点的继电器。 控制器可以识别监控电路中的交叉短路、电缆断裂和接地泄漏。 开关设置：交叉线短路检测功能（出厂默认值）通过模块前盖下方的开关进行编程：预设nQS（顶部）：无交叉线短路保护，适用于单通道应用和控制电路中有电位输出的应用。位置QS（下）：带交叉短路保护，适用于双通道应用，控制回路中无带电势的输出端。 对于单通道控制，连接NC触点至S11/S12 并桥接S12/S22（QS开关=nQS） 将安全光栅/光幕的P型输出连接到S12/S22。设备必须具有相同的参考电位。QS-开关 = nQS 自动启动：通过将反馈回路与端子S12/X3相连来设定自动启动程序。如果无需反馈回路，则必须以桥接代替。 F1 = 混合保险丝
Schmersal India Pvt. Ltd., Plot No - G-7/1, Ranjangaon MIDC, Tal. - Shirur, Dist.- Pune 412 220
所涉及的详细信息和数据已经过仔细检查。 图像可能与原始图像有所不同。 您可在说明书中进一步获得技术数据。 可能会有技术修改和错误。
生成日期 2025/4/14 下午8:30