## Worksheet
RSS 36-SD-R-ST
| Universal coding with RFID technology 1 x connector socket M12, 8-pole Actuation from side Max. 31 sensors can be wired in series. serial diagnostic output Thermoplastic enclosure | RFID-technology for needs-based protection against tampering Misaligned actuation possible 27 mm x 108.2 mm x 35 mm High repeat accuracy of the switching points 2 short-circuit proof PNP safety outputs Integral cross-short, wire-breakage and external voltage monitoring of the safety cables up to the control cabinet
Ordering data
Product type description | RSS 36-SD-R-ST
Article number (order number) | 101217290
EAN (European Article Number) | 4030661413419
eCl@ss number, version 12.0 | 27-27-46-01
eCl@ss number, version 11.0 | 27-27-24-03
eCl@ss number, version 9.0 | 27-27-24-03
ETIM number, version 7.0 | EC001829
ETIM number, version 6.0 | EC001829
Approvals - Standards
Certificates | TÜV cULus ECOLAB FCC IC ANATEL
General data
Standards | EN ISO 13849-1 EN IEC 60947-5-3 EN IEC 61508
Coding | Universelle Codierung
Coding level according to EN ISO 14119 | gering
Working principle | RFID
Frequency band RFID | 125 kHz
Transmitter output RFID, maximum | -6 dB/m
Housing construction form | Quader
Installation conditions (mechanical) | nicht bündig
Sensor topology | Reihenschaltungsgerät
Housing material | Kunststoff, glasfaserverstärkter Thermoplast
Reaction time, maximum | 100 ms
Duration of risk, maximum | 200 ms
Reaction time, switching off safety outputs via actuator, maximum | 100 ms
Reaction time, switching off safety outputs via safety inputs, maximum | 0,5 ms
Gross weight | 100 g
General data - Features
Serial diagnostics | Ja
Latching | Ja
Short circuit detection | Ja
Cross-circuit detection | Ja
Series-wiring | Ja
Safety functions | Ja
Cascadable | Ja
Integral system diagnostics, status | Ja
Number of LEDs | 3
Number of semi-conductor outputs with signaling function | 1
Number of fail-safe digital outputs | 2
Number of series-wiring of sensors | 31
<table><tr><td>Safety classification</td></tr></table>
Vorschriften | EN ISO 13849-1 EN IEC 61508
Performance Level, up to | e
Category | 4
PFH value | 2,70 x 10⁻¹⁰ /h
PFD value | 2,10 x 10⁻⁵
Safety Integrity Level (SIL), suitable for applications in | 3
Mission time | 20 Year(s)
Mechanical data
Actuating panels | seitlich
Active area | seitlich
Mechanical life, minimum | 1.000.000 Operations
Note (Mechanical life) | Betätigungsgeschwindigkeit < 0,25 m/s Schaltspiele bei Türmassen ≤ 5 kg
Latching force, approx. | 18 N
Mounting | Zur Montage der Sensoren sowie bei seitlicher Befestigung der Betätiger reichen 25 mm Schraubenlänge. Bei hochkant montiertem Betätiger sowie bei Verwendung der Dichtungsscheiben werden 30 mm lange Schrauben empfohlen.
Type of the fixing screws | 2x M4 (Zylinderkopfschrauben mit Unterlegscheiben DIN 125A / Form A)
Tightening torque of the fixing screws, minimum | 2,2 Nm
Tightening torque of the fixing screws, maximum | 2,5 Nm
Mechanical data - Switching distances according EN IEC 60947-5-3
Switch distance, typical | 12 mm
Assured switching distance &quot;ON&quot; Sao | 10 mm
Assured switching distance &quot;OFF&quot; Sar | 20 mm
Hysteresis (Switching distance), maximum | 2 mm
Repeat accuracy R | 0,5 mm
Note (Repeat accuracy R) | Seitlicher Versatz: Die lange Seitenfläche erlaubt einen max. Höhenversatz (x) von Sensor und Betätiger um 8 mm (z.B. Montagetoleranz oder durch Absacken der Schutztür). Der Querversatz (y) beträgt max. ± 18 mm (siehe Abbildung: Funktionsweise).Mindestabstand von zwei Sensorsystemen 100 mm
Mechanical data - Connection technique
Note (length of the sensor chain) | Leitungslänge und Leitungsquerschnitt verändern den Spannungsfall in Abhängigkeit vom Ausgangsstrom
Note (series-wiring) | Anzahl der Geräte unbegrenzt, externen Leitungsschutz beachten, max. 31 Geräte bei serieller Diagnose SD
Termination | Steckverbinder M12, 8-polig
Mechanical data - Dimensions
Length of sensor | 22 mm
Width of sensor | 106,3 mm
Height of sensor | 25 mm
Ambient conditions
Degree of protection | IP65 IP67 IP69
Ambient temperature | -28 ... +70 °C
Storage and transport temperature | -28 ... +85 °C
Relative humidity, maximum | 93 %
Note (Relative humidity) | nicht kondensierend nicht vereisend
Resistance to vibrations | 10 … 55 Hz, Amplitude 1 mm
Restistance to shock | 30 g / 11 ms
Protection class | III
Permissible installation altitude above sea level, maximum | 2.000 m
Ambient conditions - Insulation values
Rated insulation voltage Ui | 32 VDC
Rated impulse withstand voltage Uimp | 0,8 kV
Overvoltage category | III
Degree of pollution | 3
Electrical data
Operating voltage | 24 VDC -15 % / +10 % (stabilisiertes PELV-Netzteil)
Operating current, minimum | 0,5 mA
No-load supply current I0, typical | 35 mA
Rated operating voltage | 24 VDC
Operating current | 600 mA
Required rated short-circuit current | 100 A
Time to readiness, maximum | 2.000 ms
Switching frequency, maximum | 1 Hz
Electrical fuse rating, maximum | 2 A
Electrical data - Safety digital inputs
Designation, Safety inputs | X1 und X2
Current consumption of the safety inputs | 5 mA
Test pulse duration, maximum | 1 ms
Test pulse interval, minimum | 100 ms
Classification ZVEI CB24I, Sink | C1
Classification ZVEI CB24I, Source | C1 C2 C3
Electrical data - Safety digital outputs
Designation, Safety outputs | Y1 und Y2
Rated operating current (safety outputs) | 250 mA
Output current, (fail-safe output), maximum | 0,25 A
Design of control elements | kurzschlussfest, p-schaltend
Voltage drop Ud, maximum | 1 V
Leakage current Ir, maximum | 0,5 mA
Voltage, Utilisation category DC-12 | 24 VDC
Current, Utilisation category DC-12 | 0,25 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 0,25 A
Test pulse interval, typical | 1000 ms
Test pulse duration, maximum | 0,3 ms
Classification ZVEI CB24I, Source | C2
Classification ZVEI CB24I, Sink | C1 C2
Electrical data - Serial diagnostic SD
Designation, Serial diagnostic SD | OUT
Operation current | 150 mA
Design of control elements | kurzschlussfest, p-schaltend
Wiring capacitance | 50 nF
Electrical data - Electromagnetic compatibility (EMC)
Interfering radiation | IEC 61000-6-4
Status indication
Note (LED switching conditions display) | gelbe LED: Betriebszustand grüne LED: Versorgungsspannung rote LED: Fehler
Pin assignment
PIN 1 | A1 Ue
PIN 2 | X1 Sicherheitseingang 1
PIN 3 | A2 GND: blau
PIN 4 | Y1 Sicherheitsausgang 1: schwarz
PIN 5 | OUT serieller Diagnoseausgang: grau
PIN 6 | X2 Sicherheitseingang 2: violett
PIN 7 | Y2 Sicherheitsausgang 2: rot
PIN 8 | IN serieller Diagnoseeingang: rosa
Scope of delivery
Scope of delivery | Der Betätiger ist nicht im Lieferumfang enthalten.
Accessory
Recommendation (actuator) | RST 36-1 RST 36-1-R
Recommended safety switchgear | PROTECT PSC1 SRB-E-301ST SRB-E-201LC
Note
Note (General) | Anforderungen an die Auswertung: Zweikanaliger Sicherheitseingang, geeignet für p-schaltende Sensoren mit Schließerfunktion. Die Funktionstests der Sensoren mit zyklischem Abschalten der Sensorausgänge für max. 1 ms müssen von der Auswertung toleriert werden. Eine Querschlusserkennung in der Auswertung ist nicht notwendig.
Schmersal India Pvt. Ltd., Plot No - G-7/1, Ranjangaon MIDC, Tal. - Shirur, Dist.- Pune 412 220
Die genannten Daten und Angaben wurden sorgfältig geprüft. Abbildungen können vom Original abweichen. Weitere technische Daten finden Sie in der Betriebsanleitung. Technische Änderungen und Irrtümer vorbehalten.
Generiert am: 03.04.2025, 17:52