## Worksheet
SRB301ST 230V
Suitable for the signal processing of outputs with contact sensors 3 safety contacts, STOP 0 1 Signalling output
Ordering data
Replacement article number | 101177167
Product type description | SRB301ST 230V
Article number (order number) | 101170099
EAN (European Article Number) | 4250116201822
eCl@ss number, version 12.0 | 27-37-18-19
eCl@ss number, version 11.0 | 27-37-18-19
eCl@ss number, version 9.0 | 27-37-18-19
ETIM number, version 7.0 | EC001449
ETIM number, version 6.0 | EC001449
Approvals - Standards
Certificates | TÜV cULus CCC
General data
Standards | EN IEC 62061 EN ISO 13849-1 EN IEC 60947-5-1 EN IEC 60947-5-3 EN IEC 60947-5-5 EN IEC 61508 EN IEC 60204-1 EN IEC 60947-1
Climatic stress | EN 60068-2-78
Housing material | Kunststoff, glasfaserverstärkter Thermoplast, belüftet
Gross weight | 250 g
General data - Features
Electronic Fuse | Ja
Wire breakage detection | Ja
Removable Terminals | Ja
Start input | Ja
Feedback circuit | Ja
Automatic reset function | Ja
Reset edge detection | Ja
Earth connection detection | Ja
Integral system diagnostics, status | Ja
Number of auxiliary contacts | 1
Number of LEDs | 3
Number of normally closed (NC) | 2
Number of safety contacts | 3
<table><tr><td>Safety classification</td></tr></table>
Vorschriften | EN IEC 60947-5-1 EN IEC 61508
Stop-Category | 0
<table><tr><td>Safety classification - Relay outputs</td></tr></table>
Performance Level, up to | e
Category | 4
Diagnostic Coverage (DC) Level | &gt; 99 %
PFH value | 2,00 x 10⁻⁸ /h
Safety Integrity Level (SIL), suitable for applications in | 3
Mission time | 20 Year(s)
Common Cause Failure (CCF), minimum | 65
Mechanical data
Mechanical life, minimum | 10.000.000 Operations
Mounting | Schnellbefestigung für Normschiene nach DIN EN 60715
Mechanical data - Connection technique
Terminal designations | IEC/EN 60947-1
Termination | starr oder flexibel Schraubanschluss M20 x 1.5
Cable section, minimum | 0,25 mm²
Cable section, maximum | 2,5 mm²
Tightening torque of Clips | 0,6 Nm
Mechanical data - Dimensions
Width | 22,5 mm
Height | 100 mm
Depth | 121 mm
Ambient conditions
Degree of protection of the enclosure | IP40
Degree of protection of the mounting space | IP54
Degree of protection of clips or terminals | IP20
Ambient temperature | -25 ... +45 °C
Storage and transport temperature | -40 ... +85 °C
Resistance to vibrations | 10 ... 55 Hz, Amplitude 0,35 mm
Restistance to shock | 30 g / 11 ms
Ambient conditions - Insulation values
Rated impulse withstand voltage Uimp | 4 kV
Overvoltage category | III
Degree of pollution | 2
Electrical data
Frequency range | 50 Hz 60 Hz
Type of voltage range | AC
Rated operating voltage | 48 ... 240 VAC
Rated AC voltage for controls, 50 Hz, minimum | 48 VAC
Rated control voltage at AC 50 Hz, maximum | 240 VAC
Rated AC voltage for controls, 60 Hz, minimum | 48 VAC
Rated control voltage at AC 60 Hz, maximum | 240 VAC
Electrical power consumption | 2,8 VA
Contact resistance, maximum | 0,1 Ω
Note (Contact resistance) | in Neuzustand
Drop-out delay in case of power failure, typically | 80 ms
Drop-out delay in case of emergency, typically | 20 ms
Pull-in delay at automatic start, maximum, typically | 100 ms
Pull-in delay at RESET, typically | 20 ms
Material of the contacts, electrical | AgSnO, selbstreinigend, zwangsgeführt
Electrical data - Safe relay outputs
Voltage, Utilisation category AC-15 | 230 VAC
Current, Utilisation category AC-15 | 6 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 6 A
Switching capacity, minimum | 10 VDC
Switching capacity, minimum | 10 mA
Switching capacity, maximum | 250 VAC
Switching capacity, maximum | 8 A
Electrical data - Digital inputs
Conduction resistance, maximum | 40 Ω
Electrical data - Digital Output
Voltage, Utilisation category DC-12 | 24 VDC
Current, Utilisation category DC-12 | 0,1 A
Electrical data - Relay outputs (auxiliary contacts)
Switching capacity, maximum | 24 VDC
Switching capacity, maximum | 2 A
Electrical data - Electromagnetic compatibility (EMC)
EMC rating | EMV-Richtlinie
Status indication
Indicated operating states | Stellung der Relais K2 Stellung der Relais K1
Other data
Note (applications) | Schutzeinrichtung NOT-HALT-Taster Seilzug-Notschalter
Note
Note (General) | Induktive Verbraucher (Schütze, Relais etc.) sind durch eine geeignete Beschaltung zu entstören.
Wiring example
Note (Wiring diagram) | Das Schaltungsbeispiel ist bei geschlossenen Schutzeinrichtungen und im spannungslosen Zustand dargestellt. Eingangsebene: 2-kanalige Ansteuerung, dargestellt am Beispiel einer Schutztürüberwachung mit zwei Positionsschaltern, davon einer zwangsöffnend, externem Reset-Taster (R) und Rückführkreis (H2). Leistungsebene: 2-kanalige Ansteuerung geeignet zur Kontaktverstärkung bzw. Kontaktvervielfältigung durch Schütze oder Relais mit zwangsgeführten Kontakten. Bei 1-kanaliger Ansteuerung den Öffnerkontakt S11/S12 anschließen und S12/S22 brücken Automatischer Start: Die Programmierung auf automatischen Start erfolgt durch die Einbindung des Rückführkreises an die Klemmen S12/X3. Bei nicht benötigtem Rückführkreis ist dieser durch eine Brücke zu ersetzen. Die Ansteuerung erkennt Drahtbrüche im Überwachungskreis.
Schmersal India Pvt. Ltd., Plot No - G-7/1, Ranjangaon MIDC, Tal. - Shirur, Dist.- Pune 412 220
Die genannten Daten und Angaben wurden sorgfältig geprüft. Abbildungen können vom Original abweichen. Weitere technische Daten finden Sie in der Betriebsanleitung. Technische Änderungen und Irrtümer vorbehalten.
Generiert am: 01.05.2025, 02:40