## Worksheet
PFB-SD-4M12-SD
| For SD-Interface devices Passive field box for series-wiring For devices with M12 Connector, 8-pole For up to 4 safety switchgears | Fuse protected device ports Heavy duty version for field installation Protection class IP67
Ordering data
Product type description | PFB-SD-4M12-SD
Article number (order number) | 103013574
EAN (European Article Number) | 4030661491684
eCl@ss number, version 12.0 | 27-37-18-19
eCl@ss number, version 11.0 | 27-37-18-19
eCl@ss number, version 9.0 | 27-37-18-19
ETIM number, version 7.0 | EC001449
ETIM number, version 6.0 | EC001449
Approvals - Standards
Certificates | cULus
General data
Standards | EN IEC 60947-1
Housing material | Kunststof, polyamide PA 6 GF
Material of the identification label | Kunststof, polyamide PA
Material of viewing window | Polyamide PACM 12
Material of electronic encapsulation | Polyurethaan 2K PU
Gross weight | 443 g
General data - Features
Integral system diagnostics, status | Ja
Number of LEDs | 9
Mechanical data
Mounting | Schroeven
Type of the fixing screws | 2x M6
Tightening torque of the fixing screws, maximum | 3 Nm
Type of the fixing screws, viewing window | 2x TX10 (Torx)
Tightening torque of the fastening screws for the viewing window, maximum | 0,6 Nm
Mechanical data - Connection technique
Termination | M12 Inbouwstekker / -stekker
Terminal connector, Input/Output | X1 - X4: M12, 8-polig, A-codering
Terminal Connector, Power I/O | M12 POWER, 4-polig, T-codering
Terminal Connector, IO Signal | M12, 4-polig, A-codering
Tightening torque of electrical connection, minimum | 0,8 Nm
Tightening torque of electrical connection, maximum | 1,5 Nm
Mechanical data - Dimensions
Width | 63 mm
Height | 156,6 mm
Depth | 36,1 mm
Ambient conditions
Degree of protection | IP67
Ambient temperature | -20 ... +65 °C
Storage and transport temperature | -40 ... +70 °C
Relative humidity, minimum | 10 %
Relative humidity, maximum | 95 %
Note (Relative humidity) | niet-condenserend
Resistance to vibrations | 10 … 150 Hz, Amplitude 0,35 mm
Restistance to shock | 30 g / 11 ms
Protection class | III
Permissible installation altitude above sea level, maximum | 2.000 m
Ambient conditions - Insulation values
Rated insulation voltage Ui | 32 VDC
Rated impulse withstand voltage Uimp | 0,8 kV
Overvoltage category | III
Degree of pollution | 3
Electrical data
Operating voltage | 24 VDC -15 % / +10 %
Rated operating voltage | 24 VDC
Operating current | 10.000 mA
Note (Electrical data, Fuse rating) | Externe beveiliging vereist ≤ 10A traag bij gebruik volgens UL 61010.
Electrical data - Power supply external devices
Rated operating voltage | 24 VDC
Rated operating current | 800 mA
Internal electrical fuse | 1.5 A (Integrated automatic resettable fuse)
LED status display - LED 01
LED status | Power LED device port
LED position | P: 1 ... 4
LED colour | groen
LED status display - LED 02
LED status | Input-LED toestelaansluiting
LED position | I: 1 ... 4
LED colour | geel
LED status display - LED 08
LED status | Power-LED veldbox
LED position | &quot;Pwr&quot;: module
LED colour | groen
Schmersal India Pvt. Ltd., Plot No - G-7/1, Ranjangaon MIDC, Tal. - Shirur, Dist.- Pune 412 220
De genoemde gegevens en informatie zijn zorgvuldig gecontroleerd. Afbeeldingen kunnen afwijken van het origineel. Verdere technische gegevens zijn te vinden in de handleiding. Technische wijzigingen en fouten voorbehouden.
Gegenereerd op 15-10-2025 01:53