## Worksheet
SFB-EIP-8M12-IOP
Safety fieldbox for EtherNet/IP with CIP-Safety For connection of up to 8 safety switching devices Integrated dual-port switch Protection class IP66, IP67
Ordering data
Product type description | SFB-EIP-8M12-IOP
Article number (order number) | 103015480
EAN (European Article Number) | 4030661628691
eCl@ss number, version 12.0 | 27-24-26-04
eCl@ss number, version 11.0 | 27-24-26-04
eCl@ss number, version 9.0 | 27-24-26-04
ETIM number, version 7.0 | EC001599
ETIM number, version 6.0 | EC001599
Approvals - Standards
Certificates | TÜV cULus UKCA
General data
Standards | EN IEC 61131-1 EN IEC 61131-2 EN ISO 13849-1 EN IEC 60947-5-3 EN IEC 61508
Housing material | Plast, polyamid PA 6 GF
Material of the identification label | Plast, polyamid PA
Material of viewing window | Polyamide PACM 12
Material of electronic encapsulation | Polyurethane 2K PU
Gross weight | 649 g
General data - Features
Integral system diagnostics, general | Ja
<table><tr><td>Safety classification</td></tr></table>
Vorschriften | EN ISO 13849-1 EN IEC 61508
<table><tr><td>Safety classification - Safety inputs 2-channels</td></tr></table>
Performance Level, up to | e
Category | 4
Diagnostic Coverage (DC) Level | 99 %
PFH value | 1,10 x 10⁻⁹ /h
PFDavg | 9,60 x 10⁻⁵
Safety Integrity Level (SIL), suitable for applications in | 3
Mission time | 20 Year(s)
Response time of local safety input ⇒ Fieldbus, maximum | 20 ms
Notice | The SFB fulfils the requirements as PDDB (proximity switch with defined behaviour under fault conditions) according to EN 60947-5-3 in combination with magnetic sensors (2 NC contacts) up to PL e / SIL 3.
<table><tr><td>Safety classification - Safety inputs 1-channel</td></tr></table>
Performance Level, up to | d
Category | 2
Diagnostic Coverage (DC) Level | 90 %
PFH value | 2,30 x 10⁻⁷ /h
PFDavg | 2,00 x 10⁻²
Safety Integrity Level (SIL), suitable for applications in | 1
Mission time | 20 Year(s)
Response time of local safety input &gt; Fieldbus, maximum | 20 ms
Test interval for error detection | 10 s
<table><tr><td>Safety classification - Safety outputs 1-channel</td></tr></table>
Performance Level, up to | d
Category | 3
Diagnostic Coverage (DC) Level | 90 %
PFH value | 1,00 x 10⁻⁷ /h
PFDavg | 8,80 x 10⁻³
Safety Integrity Level (SIL), suitable for applications in | 2
Mission time | 20 Year(s)
Reaction time Fieldbus &gt; local safety output | 50 ms
<table><tr><td>Safety classification - Safety outputs 2-channels</td></tr></table>
Performance Level, up to | e
Category | 4
Diagnostic Coverage (DC) Level | 99 %
PFH value | 1,20 x 10⁻⁹ /h
PFDavg | 1,10 x 10⁻⁴
Safety Integrity Level (SIL), suitable for applications in | 3
Mission time | 20 Year(s)
Reaction time Fieldbus &gt; local safety output | 50 ms
Mechanical data
Mounting | Skruer
Type of the fixing screws | 2x M6
Tightening torque of the fixing screws, maximum | 3 Nm
Type of the fixing screws, viewing window | 2x TX10 (Torx)
Tightening torque of the fastening screws for the viewing window, maximum | 0,6 Nm
Mechanical data - Connection technique
Termination | M12 konnektorsokkel / -stik
Terminal connector, Input/Output | X0 - X7: M12, 8-polet, A-kodet
Terminal Connector, Power I/O | M12 POWER, 4-pole, T-coded
Terminal Connector, Field bus | M12, 4-pole, D-coded
Tightening torque of electrical connection, minimum | 0,8 Nm
Tightening torque of electrical connection, maximum | 1,5 Nm
Mechanical data - Dimensions
Length | 222,8 mm
Width | 63 mm
Height | 36,1 mm
Ambient conditions
Degree of protection | IP66 IP67
Ambient temperature | -25 ... +55 °C
Storage and transport temperature | -25 ... +70 °C
Relative humidity, minimum | 10 %
Relative humidity, maximum | 95 %
Note (Relative humidity) | ikke kondenserende
Resistance to vibrations | 10 … 150 Hz, Amplitude 0,35 mm / 5 g
Restistance to shock | 30 g / 11 ms
Protection class | III
Permissible installation altitude above sea level, maximum | 2 000 m
Ambient conditions - Insulation values
Rated insulation voltage Ui | 32 VDC
Rated impulse withstand voltage Uimp | 0,8 kV
Overvoltage category | III
Degree of pollution | 3
Electrical data
Operating voltage | 24 VDC -15 % / +10 %
Current consumption | 200 mA
Rated operating voltage | 24 VDC
Operating current | 10 000 mA
Note (Electrical data, Fuse rating) | External fuse protection required ≤ 10A slow blow when used to UL 61010.
Time to readiness, maximum | 12 000 ms
Device Watchdog Time | 12 ms
Reaction Time Safety Input, maximum | 20 ms
Reaction Time Safety Output, maximum | 50 ms
Electrical data - Communication protocols
Feldbus Protokoll | EtherNet/IP / CIP Safety
Fieldbus specification | V1.27
Specification safety fieldbus | V2.22
Fieldbus properties | Device Level Ring (DLR)
Transfer rate | 100 Mbit/s Full Duplex
Adressing | Dynamic Host Configuration Protocol (DHCP) / BootP
Integrated switch | Dual Port, 100 Mbit/s
Fieldbus services | LLDP
Service interface | WEB-Interface HTTP
Electrical data - Device Ports
Bezeichnung, Geräteanschlüsse | X0 ... X7
Cable length, device port | 30 m
Electrical data - Power supply external devices
Designation, Power supply | A1 and A2
Rated operating voltage | 24 VDC
Rated operating current | 800 mA
Internal electrical fuse | 1.5 A (Integrated automatic resettable fuse)
Electrical data - Safety digital inputs
Designation, Safety inputs | X1 and X2
Switching thresholds | −3 V … 5 V (Low) 13 V ... 30 V (High)
Current consumption at 24 V | 6 mA
Permissible residual drive current | 1 mA
Test pulse duration, minimum | 0,01 ms
Test pulse duration, maximum | 1 ms
Test pulse interval, minimum | 20 ms
Test pulse interval, maximum | 120 000 ms
Classification ZVEI CB24I, Sink | C1
Classification ZVEI CB24I, Source | C1 C2 C3
Electrical data - Safety digital outputs
Designation, Safety outputs | DO
Design of control elements | short-circuit proof, p-type
Voltage drop Ud, maximum | 2 V
Leakage current Ir, maximum | 0,5 mA
Voltage, Utilisation category DC-12 | 24 VDC
Current, Utilisation category DC-12 | 0,8 A
Voltage, Utilisation category DC-13 | 24 VDC
Current, Utilisation category DC-13 | 0,8 A
Note, Utilisation category DC-13 | Inductive load, maximum 400 mH
Switching frequency, maximum | 1 Hz
Test pulse duration, maximum | 1 ms
Test pulse interval, minimum | 15 ms
Test pulse interval, maximum | 500 ms
Classification ZVEI CB24I, Source | C1
Classification ZVEI CB24I, Sink | C1
Electrical data - Diagnostic inputs / FB-Interface
Designation, Diagnostic inputs / FB-Interface | DI
Switching thresholds | −3 V … 5 V (Low) 15 V … 30 V (High)
Current consumption at 24V | 12 mA
Input debounce filter | 10 ms
Data transfer rate FB-Interface | 19,2 kBaud
Electrical data - Test pulse output
Designation, Test pulse outputs | Y1 and Y2
Design of control elements | short-circuit proof, p-type
Voltage drop Ud, maximum | 1 V
Current leakage Ir, maximum | 0,5 mA
Voltage, Utilisation category DC-12 | 24 VDC
Y1 rated current at 24 V | 15 mA
Y2 rated current at 24 V | 10 mA
Y2 rated current at 0 V | 30 mA
Test pulse interval, typical | 500 ms
Test pulse duration, maximum | 1 ms
Classification ZVEI CB24I, Sink | C1
Classification ZVEI CB24I, Source | C1
LED status display - LED 01
LED status | Error LED device port
LED position | E: 0 ... 7
LED colour | grønn/rød
LED status display - LED 02
LED status | Input LED device port
LED position | I: 0 ... 7
LED colour | Gul
LED status display - LED 03
LED status | LED Link Ethernet port
LED position | L: P1 + P2
LED colour | grønn
LED status display - LED 04
LED status | LED Activity Ethernet port
LED position | A: P1 + P2
LED colour | Gul
LED status display - LED 05
LED status | Module status LED
LED position | "MS": Module
LED colour | grønn/rød
LED status display - LED 06
LED status | Network Status LED
LED position | "NS": Module
LED colour | grønn/rød
LED status display - LED 07
LED status | Fieldbox error LED
LED position | &quot;Err&quot;: Module
LED colour | grønn/rød
LED status display - LED 08
LED status | Power-LED fieldbox
LED position | &quot;Pwr&quot;: Module
LED colour | grønn
Other data
Note (applications) | Sikker feltboks med desentralisert I/Os
Schmersal India Pvt. Ltd., Plot No - G-7/1, Ranjangaon MIDC, Tal. - Shirur, Dist.- Pune 412 220
Data og verdier er kontrollert omhyggelig. Bilder kan avvike fra originalen. Ytterligere tekniske data finner du i manualen. Tekniske modifiseringer og feil kan forkomme.
Generert til 04.04.2025, 05:14